## Instructions
PID CONTROLLER SIMULATOR
This worksheet simulate a simple level control in a tank. The algoritm PID, for discrete values, is used to simulate the process:
Where:
-
-
-
-
-
-
-
It was cosidered that the controller has in input (Cin) and in output (CO) the variables according to the standard 4-20 mA.
Sampling time ∆t is equal to 1 s. The system is initially in a steady state with settable input flow rate equal to output flowrate (refer to sheet "Calculation", cell J21).
At t = 0 it takes a step disturbance on the discharge line by means of the pump (refer to sheet "Calculation", cell J24)
Through mass balance the actual level (Present Value) is calculated (refer to sheet "Calculation", cells C44:C2116). Obviously in real case there is a Level Trasmitter that "read" and communicate at the controller the PV.
It is possible to put in the system a dead time (refer to sheet "Calculation", cell J25) just to see the effect on the PID controller.
The algoritm PID determines the control action on the control valve that modify the inlet flowrate.
The control valve has a linear characteristic: Fin= % opening valve / 100 * Fmax, in.
To disable the derivative action is sufficient to set Td = 0 (refer to sheet "Calculation", cell J8) while to disable the integral action set value 0 in the cell J9, sheet "Calculation".
Note: this excel file simulates an "academic" version of the PID controller.
〖𝑪𝑶〗_𝒏= 𝑲_𝒑∗𝑬_𝒏+𝑲_𝒑 𝚫𝒕/𝑻_𝑰 ∑_(𝒊=𝟎)^(𝒊=𝒏)▒〖𝑬_𝒊+𝑲_𝒑 𝑻_𝑫/𝚫𝒕 (𝑬_𝒏−𝑬_(𝒏−𝟏) )+〖𝑪𝑶〗_𝟎 〗
, mA
〖𝐶𝑂〗_(𝑛 ):𝑐𝑜𝑛𝑡𝑟𝑜𝑙𝑙𝑒𝑟 𝑜𝑢𝑡𝑝𝑢𝑡 𝑠𝑖𝑔𝑛𝑎𝑙 𝑎𝑡 𝑛−𝑡ℎ 𝑠𝑎𝑚𝑝𝑙𝑒, mA
, mA
𝐸_(𝑛 ):𝑒𝑟𝑟𝑜𝑟 𝑎𝑡 𝑛−𝑡ℎ 𝑠𝑎𝑚𝑝𝑙𝑒, mA
, s
∆𝑡:𝑠𝑎𝑚𝑝𝑙𝑖𝑛𝑔 𝑡𝑖𝑚𝑒, s
𝐾_𝑝:𝑝𝑟𝑜𝑝𝑜𝑟𝑡𝑖𝑜𝑛𝑎𝑙 𝑎𝑐𝑡𝑖𝑜𝑛 𝑐𝑜𝑠𝑡𝑎𝑛𝑡
, s
𝑇_𝐼:𝑖𝑛𝑡𝑒𝑔𝑟𝑎𝑙 𝑎𝑐𝑡𝑖𝑜𝑛 𝑡𝑖𝑚𝑒, s
,s
𝑇_𝐷:𝑑𝑒𝑟𝑖𝑣𝑎𝑡𝑒 𝑎𝑐𝑡𝑖𝑜𝑛 𝑡𝑖𝑚𝑒,s
(t=0), mA
〖𝐶𝑂〗_0:𝑐𝑜𝑛𝑡𝑟𝑜𝑙𝑙𝑒𝑟 𝑜𝑢𝑡𝑝𝑢𝑡 𝑠𝑖𝑔𝑛𝑎𝑙 𝑎𝑡 𝑖𝑛𝑖𝑡𝑖𝑎𝑙 𝑠𝑡𝑒𝑎𝑑𝑦 𝑠𝑡𝑎𝑡𝑒 (t=0), mA

## Calculation
INPUT DATA
[9 empty] | PI |  |  |  |  | OUTPUT DATA
[8 empty] | KP | 13.9116 | [19 empty] | KP | 13.9116
[8 empty] | TI, s | 10.2825 | [19 empty] | Ti | 10.2825
[8 empty] | TD, s | 0 | [19 empty] | TD | 0
[7 empty] | Integral on(1)/off(0) |  | 1 |  |  |  |  | Direct | ------------> | E = PV - SP | If PV > SP then CO (controller output signal) increase | [11 empty] | Total | 13.1105
[7 empty] | Opening valve t=0,% |  | 40 |  |  |  |  | Indirect | ------------> | E = SP - PV | If PV > SP then CO (controller output signal) decrease | [11 empty] | Max | 0.10411
[7 empty] | Controller action |  | Indirect | [19 empty] | Jitter | 24
[29 empty] | Q1 | 2.6302e-06
[29 empty] | Q2 | 7.5426e-05
[29 empty] | Q3 | 0.0021499
[7 empty] | Control valve |  | Fail close |  |  |  |  | Fail close | ------------> | Air to open
[7 empty] | F max in, T/h |  | 50 |  |  |  |  | Fail open | ------------> | Air to close
[7 empty] | Level min, m |  | 0
[7 empty] | Level max, m |  | 10
[7 empty] | Set Point (SP), m |  | 5
[7 empty] | Fout=Fin at t=0, mc/h |  | 20
[7 empty] | Diameter, m | Diametro, m | 2.5
[7 empty] | Section, m2 |  | 4.9
[7 empty] | Disturbance, T/h |  | 15
[7 empty] | Dead time, s |  | 1
DO NOT TOUCH BELOW VALUES
P | FALSE
PD | FALSE
PI | TRUE
PI
Controller PI - SP = 5 m - Kp = 13.9115567840042 - Ti = 10.282455014264 s - Td = 0 s
[8 empty] | Error |  |  | Proportional action | Integral action | Derivative action | PID | [5 empty] | It is only used to calculate the PV; in real case PV comes from Level Transmitter
∆t = 1s | [15 empty] | CO, mA | 4 < CO < 20 | CO corr, mA | % vlv |  |  |  |  | Sum | Ei Absolute | Del PV | abs del | change of sign
t, s | t, min | PV, m | Cin, mA | SP, m | C sp, mA | % vlv | Vlv at t=0,% | 0 | 0 | 0 | [9 empty] | Fin, mc/h | D, mc/h | Fout, mc/h | Fin - Fus | 0 | 0
0 | 0 | 5 | 12 | 5 | 12 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10.4 | 4 | 10.4 | 40 | 20 | 15 | 35 | -15 | -15 | 0
1 | 0.016667 | 5 | 12 | 5 | 12 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10.4 | 4 | 10.4 | 40 | 20 | 15 | 35 | -15 | -30 | 0 | 0 | 0
2 | 0.033333 | 4.9969 | 11.9951 | 5 | 12 | 40.4673 | 40 | 0.004898 | 0.004898 | 0.004898 | 0.068138 | 0.0066267 | 0 | 0.074765 |  | 10.4748 | 4 | 10.4748 | 40.4673 | 20.2336 | 15 | 35 | -14.7664 | -44.7664 | 0.004898 | -0.0030612 | -1 | -1
3 | 0.05 | 4.9939 | 11.9902 | 5 | 12 | 40.976 | 40 | 0.0097959 | 0.014694 | 0.004898 | 0.13628 | 0.01988 | 0 | 0.15616 |  | 10.5562 | 4 | 10.5562 | 40.976 | 20.488 | 15 | 35 | -14.512 | -59.2784 | 0.0097959 | -0.0030612 | -1 | 0
4 | 0.066667 | 4.9909 | 11.9854 | 5 | 12 | 41.5188 | 40 | 0.014618 | 0.029311 | 0.0048217 | 0.20335 | 0.039657 | 0 | 0.24301 |  | 10.643 | 4 | 10.643 | 41.5188 | 20.7594 | 15 | 35 | -14.2406 | -73.519 | 0.014618 | -0.0030135 | -1 | 0
5 | 0.083333 | 4.9879 | 11.9806 | 5 | 12 | 42.0945 | 40 | 0.019356 | 0.048668 | 0.0047386 | 0.26927 | 0.065844 | 0 | 0.33512 |  | 10.7351 | 4 | 10.7351 | 42.0945 | 21.0472 | 15 | 35 | -13.9528 | -87.4717 | 0.019356 | -0.0029616 | -1 | 0
6 | 0.1 | 4.985 | 11.976 | 5 | 12 | 42.7018 | 40 | 0.024006 | 0.072674 | 0.00465 | 0.33396 | 0.098323 | 0 | 0.43229 |  | 10.8323 | 4 | 10.8323 | 42.7018 | 21.3509 | 15 | 35 | -13.6491 | -101.1208 | 0.024006 | -0.0029062 | -1 | 0
7 | 0.11667 | 4.9821 | 11.9714 | 5 | 12 | 43.3394 | 40 | 0.028562 | 0.10124 | 0.004556 | 0.39734 | 0.13697 | 0 | 0.53431 |  | 10.9343 | 4 | 10.9343 | 43.3394 | 21.6697 | 15 | 35 | -13.3303 | -114.4511 | 0.028562 | -0.0028475 | -1 | 0
8 | 0.13333 | 4.9794 | 11.967 | 5 | 12 | 44.0062 | 40 | 0.033019 | 0.13426 | 0.0044569 | 0.45935 | 0.18164 | 0 | 0.64099 |  | 11.041 | 4 | 11.041 | 44.0062 | 22.0031 | 15 | 35 | -12.9969 | -127.448 | 0.033019 | -0.0027855 | -1 | 0
9 | 0.15 | 4.9766 | 11.9626 | 5 | 12 | 44.7006 | 40 | 0.037372 | 0.17163 | 0.0043527 | 0.5199 | 0.2322 | 0 | 0.7521 |  | 11.1521 | 4 | 11.1521 | 44.7006 | 22.3503 | 15 | 35 | -12.6497 | -140.0977 | 0.037372 | -0.0027205 | -1 | 0
10 | 0.16667 | 4.974 | 11.9584 | 5 | 12 | 45.4215 | 40 | 0.041616 | 0.21324 | 0.0042439 | 0.57894 | 0.2885 | 0 | 0.86744 |  | 11.2674 | 4 | 11.2674 | 45.4215 | 22.7108 | 15 | 35 | -12.2892 | -152.3869 | 0.041616 | -0.0026524 | -1 | 0
11 | 0.18333 | 4.9714 | 11.9543 | 5 | 12 | 46.1675 | 40 | 0.045746 | 0.25899 | 0.0041305 | 0.6364 | 0.3504 | 0 | 0.9868 |  | 11.3868 | 4 | 11.3868 | 46.1675 | 23.0837 | 15 | 35 | -11.9163 | -164.3032 | 0.045746 | -0.0025816 | -1 | 0
12 | 0.2 | 4.9689 | 11.9502 | 5 | 12 | 46.9371 | 40 | 0.049759 | 0.30875 | 0.0040128 | 0.69223 | 0.41772 | 0 | 1.1099 |  | 11.5099 | 4 | 11.5099 | 46.9371 | 23.4686 | 15 | 35 | -11.5314 | -175.8346 | 0.049759 | -0.002508 | -1 | 0
13 | 0.21667 | 4.9665 | 11.9463 | 5 | 12 | 47.7291 | 40 | 0.05365 | 0.3624 | 0.003891 | 0.74636 | 0.4903 | 0 | 1.2367 |  | 11.6367 | 4 | 11.6367 | 47.7291 | 23.8646 | 15 | 35 | -11.1354 | -186.9701 | 0.05365 | -0.0024319 | -1 | 0
14 | 0.23333 | 4.9641 | 11.9426 | 5 | 12 | 48.542 | 40 | 0.057415 | 0.41981 | 0.0037654 | 0.79874 | 0.56798 | 0 | 1.3667 |  | 11.7667 | 4 | 11.7667 | 48.542 | 24.271 | 15 | 35 | -10.729 | -197.6991 | 0.057415 | -0.0023534 | -1 | 0
15 | 0.25 | 4.9618 | 11.9389 | 5 | 12 | 49.3744 | 40 | 0.061051 | 0.48086 | 0.0036361 | 0.84932 | 0.65058 | 0 | 1.4999 |  | 11.8999 | 4 | 11.8999 | 49.3744 | 24.6872 | 15 | 35 | -10.3128 | -208.0119 | 0.061051 | -0.0022725 | -1 | 0
16 | 0.26667 | 4.9597 | 11.9354 | 5 | 12 | 50.2249 | 40 | 0.064555 | 0.54542 | 0.0035033 | 0.89806 | 0.73792 | 0 | 1.636 |  | 12.036 | 4 | 12.036 | 50.2249 | 25.1124 | 15 | 35 | -9.8876 | -217.8994 | 0.064555 | -0.0021896 | -1 | 0
17 | 0.28333 | 4.9575 | 11.9321 | 5 | 12 | 51.092 | 40 | 0.067922 | 0.61334 | 0.0033674 | 0.9449 | 0.82982 | 0 | 1.7747 |  | 12.1747 | 4 | 12.1747 | 51.092 | 25.546 | 15 | 35 | -9.454 | -227.3534 | 0.067922 | -0.0021047 | -1 | 0
18 | 0.3 | 4.9555 | 11.9288 | 5 | 12 | 51.9744 | 40 | 0.071151 | 0.68449 | 0.0032286 | 0.98982 | 0.92608 | 0 | 1.9159 |  | 12.3159 | 4 | 12.3159 | 51.9744 | 25.9872 | 15 | 35 | -9.0128 | -236.3663 | 0.071151 | -0.0020179 | -1 | 0
19 | 0.31667 | 4.9536 | 11.9258 | 5 | 12 | 52.8705 | 40 | 0.074238 | 0.75873 | 0.003087 | 1.0328 | 1.0265 | 0 | 2.0593 |  | 12.4593 | 4 | 12.4593 | 52.8705 | 26.4353 | 15 | 35 | -8.5647 | -244.931 | 0.074238 | -0.0019294 | -1 | 0
20 | 0.33333 | 4.9518 | 11.9228 | 5 | 12 | 53.779 | 40 | 0.077181 | 0.83591 | 0.002943 | 1.0737 | 1.1309 | 0 | 2.2046 |  | 12.6046 | 4 | 12.6046 | 53.779 | 26.8895 | 15 | 35 | -8.1105 | -253.0415 | 0.077181 | -0.0018394 | -1 | 0
21 | 0.35 | 4.95 | 11.92 | 5 | 12 | 54.6985 | 40 | 0.079977 | 0.91589 | 0.0027967 | 1.1126 | 1.2391 | 0 | 2.3518 |  | 12.7518 | 4 | 12.7518 | 54.6985 | 27.3492 | 15 | 35 | -7.6508 | -260.6923 | 0.079977 | -0.0017479 | -1 | 0
22 | 0.36667 | 4.9484 | 11.9174 | 5 | 12 | 55.6274 | 40 | 0.082626 | 0.99851 | 0.0026483 | 1.1495 | 1.3509 | 0 | 2.5004 |  | 12.9004 | 4 | 12.9004 | 55.6274 | 27.8137 | 15 | 35 | -7.1863 | -267.8786 | 0.082626 | -0.0016552 | -1 | 0
23 | 0.38333 | 4.9468 | 11.9149 | 5 | 12 | 56.5644 | 40 | 0.085124 | 1.0836 | 0.0024982 | 1.1842 | 1.4661 | 0 | 2.6503 |  | 13.0503 | 4 | 13.0503 | 56.5644 | 28.2822 | 15 | 35 | -6.7178 | -274.5964 | 0.085124 | -0.0015614 | -1 | 0
24 | 0.4 | 4.9453 | 11.9125 | 5 | 12 | 57.5081 | 40 | 0.087471 | 1.1711 | 0.0023465 | 1.2169 | 1.5844 | 0 | 2.8013 |  | 13.2013 | 4 | 13.2013 | 57.5081 | 28.754 | 15 | 35 | -6.246 | -280.8423 | 0.087471 | -0.0014666 | -1 | 0
25 | 0.41667 | 4.944 | 11.9103 | 5 | 12 | 58.457 | 40 | 0.089664 | 1.2608 | 0.0021936 | 1.2474 | 1.7058 | 0 | 2.9531 |  | 13.3531 | 4 | 13.3531 | 58.457 | 29.2285 | 15 | 35 | -5.7715 | -286.6138 | 0.089664 | -0.001371 | -1 | 0
26 | 0.43333 | 4.9427 | 11.9083 | 5 | 12 | 59.4098 | 40 | 0.091704 | 1.3525 | 0.0020395 | 1.2757 | 1.8298 | 0 | 3.1056 |  | 13.5056 | 4 | 13.5056 | 59.4098 | 29.7049 | 15 | 35 | -5.2951 | -291.9089 | 0.091704 | -0.0012747 | -1 | 0
27 | 0.45 | 4.9415 | 11.9064 | 5 | 12 | 60.365 | 40 | 0.093588 | 1.4461 | 0.0018846 | 1.302 | 1.9564 | 0 | 3.2584 |  | 13.6584 | 4 | 13.6584 | 60.365 | 30.1825 | 15 | 35 | -4.8175 | -296.7264 | 0.093588 | -0.0011779 | -1 | 0
28 | 0.46667 | 4.9404 | 11.9047 | 5 | 12 | 61.3213 | 40 | 0.095317 | 1.5414 | 0.001729 | 1.326 | 2.0854 | 0 | 3.4114 |  | 13.8114 | 4 | 13.8114 | 61.3213 | 30.6607 | 15 | 35 | -4.3393 | -301.0658 | 0.095317 | -0.0010806 | -1 | 0
29 | 0.48333 | 4.9394 | 11.9031 | 5 | 12 | 62.2774 | 40 | 0.09689 | 1.6383 | 0.0015731 | 1.3479 | 2.2165 | 0 | 3.5644 |  | 13.9644 | 4 | 13.9644 | 62.2774 | 31.1387 | 15 | 35 | -3.8613 | -304.9271 | 0.09689 | -0.00098316 | -1 | 0
30 | 0.5 | 4.9386 | 11.9017 | 5 | 12 | 63.2319 | 40 | 0.098307 | 1.7366 | 0.0014169 | 1.3676 | 2.3495 | 0 | 3.7171 |  | 14.1171 | 4 | 14.1171 | 63.2319 | 31.6159 | 15 | 35 | -3.3841 | -308.3112 | 0.098307 | -0.00088558 | -1 | 0
31 | 0.51667 | 4.9378 | 11.9004 | 5 | 12 | 64.1834 | 40 | 0.099568 | 1.8361 | 0.0012608 | 1.3851 | 2.4842 | 0 | 3.8693 |  | 14.2693 | 4 | 14.2693 | 64.1834 | 32.0917 | 15 | 35 | -2.9083 | -311.2195 | 0.099568 | -0.00078802 | -1 | 0
32 | 0.53333 | 4.9371 | 11.8993 | 5 | 12 | 65.1308 | 40 | 0.10067 | 1.9368 | 0.001105 | 1.4005 | 2.6204 | 0 | 4.0209 |  | 14.4209 | 4 | 14.4209 | 65.1308 | 32.5654 | 15 | 35 | -2.4346 | -313.6541 | 0.10067 | -0.00069063 | -1 | 0
33 | 0.55 | 4.9365 | 11.8984 | 5 | 12 | 66.0726 | 40 | 0.10162 | 2.0384 | 0.00094965 | 1.4137 | 2.7579 | 0 | 4.1716 |  | 14.5716 | 4 | 14.5716 | 66.0726 | 33.0363 | 15 | 35 | -1.9637 | -315.6178 | 0.10162 | -0.00059353 | -1 | 0
34 | 0.56667 | 4.936 | 11.8976 | 5 | 12 | 67.0078 | 40 | 0.10242 | 2.1409 | 0.00079498 | 1.4248 | 2.8965 | 0 | 4.3212 |  | 14.7212 | 4 | 14.7212 | 67.0078 | 33.5039 | 15 | 35 | -1.4961 | -317.1139 | 0.10242 | -0.00049686 | -1 | 0
35 | 0.58333 | 4.9356 | 11.8969 | 5 | 12 | 67.935 | 40 | 0.10306 | 2.2439 | 0.0006412 | 1.4337 | 3.0359 | 0 | 4.4696 |  | 14.8696 | 4 | 14.8696 | 67.935 | 33.9675 | 15 | 35 | -1.0325 | -318.1464 | 0.10306 | -0.00040075 | -1 | 0
36 | 0.6 | 4.9353 | 11.8965 | 5 | 12 | 68.8531 | 40 | 0.10355 | 2.3475 | 0.00048852 | 1.4405 | 3.176 | 0 | 4.6165 |  | 15.0165 | 4 | 15.0165 | 68.8531 | 34.4265 | 15 | 35 | -0.57347 | -318.7198 | 0.10355 | -0.00030533 | -1 | 0
37 | 0.61667 | 4.9351 | 11.8961 | 5 | 12 | 69.7608 | 40 | 0.10388 | 2.4514 | 0.00033714 | 1.4452 | 3.3165 | 0 | 4.7617 |  | 15.1617 | 4 | 15.1617 | 69.7608 | 34.8804 | 15 | 35 | -0.11959 | -318.8394 | 0.10388 | -0.00021071 | -1 | 0
38 | 0.63333 | 4.935 | 11.8959 | 5 | 12 | 70.6571 | 40 | 0.10407 | 2.5554 | 0.00018725 | 1.4478 | 3.4573 | 0 | 4.9051 |  | 15.3051 | 4 | 15.3051 | 70.6571 | 35.3286 | 15 | 35 | 0.32856 | -318.5109 | 0.10407 | -0.00011703 | -1 | 0
39 | 0.65 | 4.9349 | 11.8959 | 5 | 12 | 71.5409 | 40 | 0.10411 | 2.6595 | 3.9051e-05 | 1.4483 | 3.5982 | 0 | 5.0465 |  | 15.4465 | 4 | 15.4465 | 71.5409 | 35.7704 | 15 | 35 | 0.77043 | -317.7404 | 0.10411 | -2.4407e-05 | -1 | 0
40 | 0.66667 | 4.935 | 11.896 | 5 | 12 | 72.411 | 40 | 0.104 | 2.7635 | -0.00010728 | 1.4469 | 3.7389 | 0 | 5.1858 |  | 15.5858 | 4 | 15.5858 | 72.411 | 36.2055 | 15 | 35 | 1.2055 | -316.5349 | 0.104 | 6.7052e-05 | 1 | 2
41 | 0.68333 | 4.9352 | 11.8962 | 5 | 12 | 73.2664 | 40 | 0.10375 | 2.8673 | -0.00025157 | 1.4434 | 3.8793 | 0 | 5.3226 |  | 15.7226 | 4 | 15.7226 | 73.2664 | 36.6332 | 15 | 35 | 1.6332 | -314.9017 | 0.10375 | 0.00015723 | 1 | 0
42 | 0.7 | 4.9354 | 11.8966 | 5 | 12 | 74.1062 | 40 | 0.10336 | 2.9706 | -0.00039363 | 1.4379 | 4.0191 | 0 | 5.457 |  | 15.857 | 4 | 15.857 | 74.1062 | 37.0531 | 15 | 35 | 2.0531 | -312.8487 | 0.10336 | 0.00024602 | 1 | 0
43 | 0.71667 | 4.9357 | 11.8972 | 5 | 12 | 74.9293 | 40 | 0.10283 | 3.0735 | -0.00053329 | 1.4305 | 4.1582 | 0 | 5.5887 |  | 15.9887 | 4 | 15.9887 | 74.9293 | 37.4646 | 15 | 35 | 2.4646 | -310.384 | 0.10283 | 0.00033331 | 1 | 0
44 | 0.73333 | 4.9362 | 11.8978 | 5 | 12 | 75.7348 | 40 | 0.10215 | 3.1756 | -0.0006704 | 1.4211 | 4.2964 | 0 | 5.7176 |  | 16.1176 | 4 | 16.1176 | 75.7348 | 37.8674 | 15 | 35 | 2.8674 | -307.5166 | 0.10215 | 0.000419 | 1 | 0
45 | 0.75 | 4.9367 | 11.8987 | 5 | 12 | 76.5218 | 40 | 0.10135 | 3.277 | -0.00080478 | 1.4099 | 4.4336 | 0 | 5.8435 |  | 16.2435 | 4 | 16.2435 | 76.5218 | 38.2609 | 15 | 35 | 3.2609 | -304.2557 | 0.10135 | 0.00050299 | 1 | 0
46 | 0.76667 | 4.9372 | 11.8996 | 5 | 12 | 77.2895 | 40 | 0.10041 | 3.3774 | -0.00093629 | 1.3969 | 4.5694 | 0 | 5.9663 |  | 16.3663 | 4 | 16.3663 | 77.2895 | 38.6448 | 15 | 35 | 3.6448 | -300.6109 | 0.10041 | 0.00058518 | 1 | 0
47 | 0.78333 | 4.9379 | 11.9007 | 5 | 12 | 78.037 | 40 | 0.099349 | 3.4767 | -0.0010648 | 1.3821 | 4.7038 | 0 | 6.0859 |  | 16.4859 | 4 | 16.4859 | 78.037 | 39.0185 | 15 | 35 | 4.0185 | -296.5924 | 0.099349 | 0.00066549 | 1 | 0
48 | 0.8 | 4.9387 | 11.9018 | 5 | 12 | 78.7635 | 40 | 0.098159 | 3.5749 | -0.0011901 | 1.3655 | 4.8366 | 0 | 6.2022 |  | 16.6022 | 4 | 16.6022 | 78.7635 | 39.3818 | 15 | 35 | 4.3818 | -292.2107 | 0.098159 | 0.00074383 | 1 | 0
49 | 0.81667 | 4.9395 | 11.9032 | 5 | 12 | 79.4684 | 40 | 0.096847 | 3.6717 | -0.0013122 | 1.3473 | 4.9677 | 0 | 6.3149 |  | 16.7149 | 4 | 16.7149 | 79.4684 | 39.7342 | 15 | 35 | 4.7342 | -287.4765 | 0.096847 | 0.0008201 | 1 | 0
50 | 0.83333 | 4.9404 | 11.9046 | 5 | 12 | 80.1508 | 40 | 0.095416 | 3.7672 | -0.0014308 | 1.3274 | 5.0967 | 0 | 6.4241 |  | 16.8241 | 4 | 16.8241 | 80.1508 | 40.0754 | 15 | 35 | 5.0754 | -282.4011 | 0.095416 | 0.00089424 | 1 | 0
51 | 0.85 | 4.9413 | 11.9061 | 5 | 12 | 80.8101 | 40 | 0.09387 | 3.861 | -0.0015459 | 1.3059 | 5.2237 | 0 | 6.5296 |  | 16.9296 | 4 | 16.9296 | 80.8101 | 40.4051 | 15 | 35 | 5.4051 | -276.996 | 0.09387 | 0.00096616 | 1 | 0
52 | 0.86667 | 4.9424 | 11.9078 | 5 | 12 | 81.4458 | 40 | 0.092213 | 3.9532 | -0.0016573 | 1.2828 | 5.3485 | 0 | 6.6313 |  | 17.0313 | 4 | 17.0313 | 81.4458 | 40.7229 | 15 | 35 | 5.7229 | -271.2731 | 0.092213 | 0.0010358 | 1 | 0
53 | 0.88333 | 4.9435 | 11.9096 | 5 | 12 | 82.0572 | 40 | 0.090448 | 4.0437 | -0.0017649 | 1.2583 | 5.4709 | 0 | 6.7291 |  | 17.1291 | 4 | 17.1291 | 82.0572 | 41.0286 | 15 | 35 | 6.0286 | -265.2445 | 0.090448 | 0.0011031 | 1 | 0
54 | 0.9 | 4.9446 | 11.9114 | 5 | 12 | 82.6437 | 40 | 0.088579 | 4.1323 | -0.0018687 | 1.2323 | 5.5907 | 0 | 6.823 |  | 17.223 | 4 | 17.223 | 82.6437 | 41.3218 | 15 | 35 | 6.3218 | -258.9227 | 0.088579 | 0.0011679 | 1 | 0
55 | 0.91667 | 4.9459 | 11.9134 | 5 | 12 | 83.2049 | 40 | 0.08661 | 4.2189 | -0.0019685 | 1.2049 | 5.7079 | 0 | 6.9128 |  | 17.3128 | 4 | 17.3128 | 83.2049 | 41.6024 | 15 | 35 | 6.6024 | -252.3202 | 0.08661 | 0.0012303 | 1 | 0
56 | 0.93333 | 4.9472 | 11.9155 | 5 | 12 | 83.7403 | 40 | 0.084546 | 4.3034 | -0.0020643 | 1.1762 | 5.8223 | 0 | 6.9985 |  | 17.3985 | 4 | 17.3985 | 83.7403 | 41.8702 | 15 | 35 | 6.8702 | -245.4501 | 0.084546 | 0.0012902 | 1 | 0
57 | 0.95 | 4.9485 | 11.9176 | 5 | 12 | 84.2496 | 40 | 0.08239 | 4.3858 | -0.0021559 | 1.1462 | 5.9338 | 0 | 7.0799 |  | 17.4799 | 4 | 17.4799 | 84.2496 | 42.1248 | 15 | 35 | 7.1248 | -238.3253 | 0.08239 | 0.0013474 | 1 | 0
58 | 0.96667 | 4.9499 | 11.9199 | 5 | 12 | 84.7322 | 40 | 0.080147 | 4.466 | -0.0022433 | 1.115 | 6.0422 | 0 | 7.1572 |  | 17.5572 | 4 | 17.5572 | 84.7322 | 42.3661 | 15 | 35 | 7.3661 | -230.9592 | 0.080147 | 0.0014021 | 1 | 0
59 | 0.98333 | 4.9514 | 11.9222 | 5 | 12 | 85.188 | 40 | 0.077821 | 4.5438 | -0.0023265 | 1.0826 | 6.1475 | 0 | 7.2301 |  | 17.6301 | 4 | 17.6301 | 85.188 | 42.594 | 15 | 35 | 7.594 | -223.3652 | 0.077821 | 0.001454 | 1 | 0
60 | 1 | 4.9529 | 11.9246 | 5 | 12 | 85.6166 | 40 | 0.075415 | 4.6192 | -0.0024053 | 1.0491 | 6.2495 | 0 | 7.2986 |  | 17.6986 | 4 | 17.6986 | 85.6166 | 42.8083 | 15 | 35 | 7.8083 | -215.5569 | 0.075415 | 0.0015033 | 1 | 0
61 | 1.0167 | 4.9544 | 11.9271 | 5 | 12 | 86.0177 | 40 | 0.072936 | 4.6921 | -0.0024797 | 1.0146 | 6.3482 | 0 | 7.3628 |  | 17.7628 | 4 | 17.7628 | 86.0177 | 43.0088 | 15 | 35 | 8.0088 | -207.5481 | 0.072936 | 0.0015498 | 1 | 0
62 | 1.0333 | 4.956 | 11.9296 | 5 | 12 | 86.3912 | 40 | 0.070386 | 4.7625 | -0.0025496 | 0.97918 | 6.4434 | 0 | 7.4226 |  | 17.8226 | 4 | 17.8226 | 86.3912 | 43.1956 | 15 | 35 | 8.1956 | -199.3525 | 0.070386 | 0.0015935 | 1 | 0
63 | 1.05 | 4.9576 | 11.9322 | 5 | 12 | 86.7369 | 40 | 0.067771 | 4.8303 | -0.0026151 | 0.9428 | 6.5351 | 0 | 7.4779 |  | 17.8779 | 4 | 17.8779 | 86.7369 | 43.3684 | 15 | 35 | 8.3684 | -190.984 | 0.067771 | 0.0016345 | 1 | 0
64 | 1.0667 | 4.9593 | 11.9349 | 5 | 12 | 87.0546 | 40 | 0.065095 | 4.8954 | -0.0026761 | 0.90557 | 6.6232 | 0 | 7.5287 |  | 17.9287 | 4 | 17.9287 | 87.0546 | 43.5273 | 15 | 35 | 8.5273 | -182.4567 | 0.065095 | 0.0016726 | 1 | 0
65 | 1.0833 | 4.961 | 11.9376 | 5 | 12 | 87.3444 | 40 | 0.062362 | 4.9577 | -0.0027325 | 0.86755 | 6.7075 | 0 | 7.5751 |  | 17.9751 | 4 | 17.9751 | 87.3444 | 43.6722 | 15 | 35 | 8.6722 | -173.7845 | 0.062362 | 0.0017078 | 1 | 0
66 | 1.1 | 4.9628 | 11.9404 | 5 | 12 | 87.606 | 40 | 0.059578 | 5.0173 | -0.0027844 | 0.82882 | 6.7881 | 0 | 7.617 |  | 18.017 | 4 | 18.017 | 87.606 | 43.803 | 15 | 35 | 8.803 | -164.9815 | 0.059578 | 0.0017403 | 1 | 0
67 | 1.1167 | 4.9645 | 11.9433 | 5 | 12 | 87.8397 | 40 | 0.056746 | 5.0741 | -0.0028317 | 0.78942 | 6.8649 | 0 | 7.6543 |  | 18.0543 | 4 | 18.0543 | 87.8397 | 43.9198 | 15 | 35 | 8.9198 | -156.0617 | 0.056746 | 0.0017698 | 1 | 0
68 | 1.1333 | 4.9663 | 11.9461 | 5 | 12 | 88.0453 | 40 | 0.053872 | 5.1279 | -0.0028745 | 0.74944 | 6.9378 | 0 | 7.6872 |  | 18.0872 | 4 | 18.0872 | 88.0453 | 44.0226 | 15 | 35 | 9.0226 | -147.0391 | 0.053872 | 0.0017965 | 1 | 0
69 | 1.15 | 4.9682 | 11.949 | 5 | 12 | 88.2229 | 40 | 0.050959 | 5.1789 | -0.0029126 | 0.70892 | 7.0068 | 0 | 7.7157 |  | 18.1157 | 4 | 18.1157 | 88.2229 | 44.1115 | 15 | 35 | 9.1115 | -137.9276 | 0.050959 | 0.0018204 | 1 | 0
70 | 1.1667 | 4.97 | 11.952 | 5 | 12 | 88.3728 | 40 | 0.048013 | 5.2269 | -0.0029462 | 0.66793 | 7.0717 | 0 | 7.7396 |  | 18.1396 | 4 | 18.1396 | 88.3728 | 44.1864 | 15 | 35 | 9.1864 | -128.7412 | 0.048013 | 0.0018414 | 1 | 0
71 | 1.1833 | 4.9719 | 11.955 | 5 | 12 | 88.4949 | 40 | 0.045038 | 5.272 | -0.0029752 | 0.62654 | 7.1326 | 0 | 7.7592 |  | 18.1592 | 4 | 18.1592 | 88.4949 | 44.2475 | 15 | 35 | 9.2475 | -119.4938 | 0.045038 | 0.0018595 | 1 | 0
72 | 1.2 | 4.9737 | 11.958 | 5 | 12 | 88.5896 | 40 | 0.042038 | 5.314 | -0.0029996 | 0.58481 | 7.1895 | 0 | 7.7743 |  | 18.1743 | 4 | 18.1743 | 88.5896 | 44.2948 | 15 | 35 | 9.2948 | -110.199 | 0.042038 | 0.0018748 | 1 | 0
73 | 1.2167 | 4.9756 | 11.961 | 5 | 12 | 88.657 | 40 | 0.039018 | 5.353 | -0.0030196 | 0.54281 | 7.2423 | 0 | 7.7851 |  | 18.1851 | 4 | 18.1851 | 88.657 | 44.3285 | 15 | 35 | 9.3285 | -100.8705 | 0.039018 | 0.0018872 | 1 | 0
74 | 1.2333 | 4.9775 | 11.964 | 5 | 12 | 88.6973 | 40 | 0.035983 | 5.389 | -0.003035 | 0.50058 | 7.291 | 0 | 7.7916 |  | 18.1916 | 4 | 18.1916 | 88.6973 | 44.3487 | 15 | 35 | 9.3487 | -91.5218 | 0.035983 | 0.0018969 | 1 | 0
75 | 1.25 | 4.9794 | 11.9671 | 5 | 12 | 88.711 | 40 | 0.032937 | 5.4219 | -0.003046 | 0.45821 | 7.3356 | 0 | 7.7938 |  | 18.1938 | 4 | 18.1938 | 88.711 | 44.3555 | 15 | 35 | 9.3555 | -82.1663 | 0.032937 | 0.0019038 | 1 | 0
76 | 1.2667 | 4.9813 | 11.9701 | 5 | 12 | 88.6983 | 40 | 0.029885 | 5.4518 | -0.0030526 | 0.41574 | 7.376 | 0 | 7.7917 |  | 18.1917 | 4 | 18.1917 | 88.6983 | 44.3491 | 15 | 35 | 9.3491 | -72.8172 | 0.029885 | 0.0019079 | 1 | 0
77 | 1.2833 | 4.9832 | 11.9732 | 5 | 12 | 88.6596 | 40 | 0.02683 | 5.4786 | -0.0030549 | 0.37324 | 7.4123 | 0 | 7.7855 |  | 18.1855 | 4 | 18.1855 | 88.6596 | 44.3298 | 15 | 35 | 9.3298 | -63.4874 | 0.02683 | 0.0019093 | 1 | 0
78 | 1.3 | 4.9851 | 11.9762 | 5 | 12 | 88.5952 | 40 | 0.023777 | 5.5024 | -0.0030528 | 0.33078 | 7.4445 | 0 | 7.7752 |  | 18.1752 | 4 | 18.1752 | 88.5952 | 44.2976 | 15 | 35 | 9.2976 | -54.1898 | 0.023777 | 0.001908 | 1 | 0
79 | 1.3167 | 4.987 | 11.9793 | 5 | 12 | 88.5056 | 40 | 0.020731 | 5.5232 | -0.0030465 | 0.28839 | 7.4725 | 0 | 7.7609 |  | 18.1609 | 4 | 18.1609 | 88.5056 | 44.2528 | 15 | 35 | 9.2528 | -44.937 | 0.020731 | 0.001904 | 1 | 0
80 | 1.3333 | 4.9889 | 11.9823 | 5 | 12 | 88.3912 | 40 | 0.017695 | 5.5408 | -0.0030359 | 0.24616 | 7.4964 | 0 | 7.7426 |  | 18.1426 | 4 | 18.1426 | 88.3912 | 44.1956 | 15 | 35 | 9.1956 | -35.7414 | 0.017695 | 0.0018975 | 1 | 0
81 | 1.35 | 4.9908 | 11.9853 | 5 | 12 | 88.2526 | 40 | 0.014673 | 5.5555 | -0.0030213 | 0.20413 | 7.5163 | 0 | 7.7204 |  | 18.1204 | 4 | 18.1204 | 88.2526 | 44.1263 | 15 | 35 | 9.1263 | -26.6151 | 0.014673 | 0.0018883 | 1 | 0
82 | 1.3667 | 4.9927 | 11.9883 | 5 | 12 | 88.0902 | 40 | 0.011671 | 5.5672 | -0.0030027 | 0.16236 | 7.5321 | 0 | 7.6944 |  | 18.0944 | 4 | 18.0944 | 88.0902 | 44.0451 | 15 | 35 | 9.0451 | -17.5699 | 0.011671 | 0.0018767 | 1 | 0
83 | 1.3833 | 4.9946 | 11.9913 | 5 | 12 | 87.9046 | 40 | 0.0086906 | 5.5759 | -0.00298 | 0.1209 | 7.5438 | 0 | 7.6647 |  | 18.0647 | 4 | 18.0647 | 87.9046 | 43.9523 | 15 | 35 | 8.9523 | -8.6176 | 0.0086906 | 0.0018625 | 1 | 0
84 | 1.4 | 4.9964 | 11.9943 | 5 | 12 | 87.6963 | 40 | 0.0057371 | 5.5816 | -0.0029535 | 0.079812 | 7.5516 | 0 | 7.6314 |  | 18.0314 | 4 | 18.0314 | 87.6963 | 43.8482 | 15 | 35 | 8.8482 | 0.23055 | 0.0057371 | 0.0018459 | 1 | 0
85 | 1.4167 | 4.9982 | 11.9972 | 5 | 12 | 87.466 | 40 | 0.0028139 | 5.5844 | -0.0029232 | 0.039146 | 7.5554 | 0 | 7.5946 |  | 17.9946 | 4 | 17.9946 | 87.466 | 43.733 | 15 | 35 | 8.733 | 8.9635 | 0.0028139 | 0.001827 | 1 | 0
86 | 1.4333 | 5 | 12.0001 | 5 | 12 | 87.2141 | 40 | -7.528e-05 | 5.5844 | -0.0028892 | -0.0010473 | 7.5553 | 0 | 7.5543 |  | 17.9543 | 4 | 17.9543 | 87.2141 | 43.6071 | 15 | 35 | 8.6071 | 17.5706 | 7.528e-05 | 0.0018057 | 1 | 0
87 | 1.45 | 5.0018 | 12.0029 | 5 | 12 | 86.9414 | 40 | -0.0029269 | 5.5814 | -0.0028516 | -0.040717 | 7.5513 | 0 | 7.5106 |  | 17.9106 | 4 | 17.9106 | 86.9414 | 43.4707 | 15 | 35 | 8.4707 | 26.0413 | 0.0029269 | 0.0017822 | 1 | 0
88 | 1.4667 | 5.0036 | 12.0057 | 5 | 12 | 86.6486 | 40 | -0.0057373 | 5.5757 | -0.0028105 | -0.079815 | 7.5436 | 0 | 7.4638 |  | 17.8638 | 4 | 17.8638 | 86.6486 | 43.3243 | 15 | 35 | 8.3243 | 34.3656 | 0.0057373 | 0.0017565 | 1 | 0
89 | 1.4833 | 5.0053 | 12.0085 | 5 | 12 | 86.3362 | 40 | -0.0085033 | 5.5672 | -0.0027659 | -0.11829 | 7.5321 | 0 | 7.4138 |  | 17.8138 | 4 | 17.8138 | 86.3362 | 43.1681 | 15 | 35 | 8.1681 | 42.5337 | 0.0085033 | 0.0017287 | 1 | 0
90 | 1.5 | 5.007 | 12.0112 | 5 | 12 | 86.0049 | 40 | -0.011221 | 5.556 | -0.0027181 | -0.15611 | 7.5169 | 0 | 7.3608 |  | 17.7608 | 4 | 17.7608 | 86.0049 | 43.0025 | 15 | 35 | 8.0025 | 50.5361 | 0.011221 | 0.0016988 | 1 | 0
91 | 1.5167 | 5.0087 | 12.0139 | 5 | 12 | 85.6556 | 40 | -0.013889 | 5.5421 | -0.0026671 | -0.19321 | 7.4981 | 0 | 7.3049 |  | 17.7049 | 4 | 17.7049 | 85.6556 | 42.8278 | 15 | 35 | 7.8278 | 58.3639 | 0.013889 | 0.001667 | 1 | 0
92 | 1.5333 | 5.0103 | 12.0165 | 5 | 12 | 85.2889 | 40 | -0.016502 | 5.5256 | -0.0026131 | -0.22956 | 7.4758 | 0 | 7.2462 |  | 17.6462 | 4 | 17.6462 | 85.2889 | 42.6444 | 15 | 35 | 7.6444 | 66.0084 | 0.016502 | 0.0016332 | 1 | 0
93 | 1.55 | 5.0119 | 12.0191 | 5 | 12 | 84.9055 | 40 | -0.019058 | 5.5065 | -0.002556 | -0.26512 | 7.45 | 0 | 7.1849 |  | 17.5849 | 4 | 17.5849 | 84.9055 | 42.4527 | 15 | 35 | 7.4527 | 73.4611 | 0.019058 | 0.0015975 | 1 | 0
94 | 1.5667 | 5.0135 | 12.0216 | 5 | 12 | 84.5062 | 40 | -0.021554 | 5.485 | -0.0024961 | -0.29985 | 7.4208 | 0 | 7.121 |  | 17.521 | 4 | 17.521 | 84.5062 | 42.2531 | 15 | 35 | 7.2531 | 80.7142 | 0.021554 | 0.0015601 | 1 | 0
95 | 1.5833 | 5.015 | 12.024 | 5 | 12 | 84.0918 | 40 | -0.023987 | 5.461 | -0.0024335 | -0.3337 | 7.3884 | 0 | 7.0547 |  | 17.4547 | 4 | 17.4547 | 84.0918 | 42.0459 | 15 | 35 | 7.0459 | 87.7601 | 0.023987 | 0.001521 | 1 | 0
96 | 1.6 | 5.0165 | 12.0264 | 5 | 12 | 83.663 | 40 | -0.026356 | 5.4346 | -0.0023684 | -0.36665 | 7.3527 | 0 | 6.9861 |  | 17.3861 | 4 | 17.3861 | 83.663 | 41.8315 | 15 | 35 | 6.8315 | 94.5916 | 0.026356 | 0.0014802 | 1 | 0
97 | 1.6167 | 5.0179 | 12.0287 | 5 | 12 | 83.2206 | 40 | -0.028656 | 5.406 | -0.0023007 | -0.39865 | 7.314 | 0 | 6.9153 |  | 17.3153 | 4 | 17.3153 | 83.2206 | 41.6103 | 15 | 35 | 6.6103 | 101.2019 | 0.028656 | 0.0014379 | 1 | 0
98 | 1.6333 | 5.0193 | 12.0309 | 5 | 12 | 82.7655 | 40 | -0.030887 | 5.3751 | -0.0022307 | -0.42969 | 7.2722 | 0 | 6.8425 |  | 17.2425 | 4 | 17.2425 | 82.7655 | 41.3828 | 15 | 35 | 6.3828 | 107.5847 | 0.030887 | 0.0013942 | 1 | 0
99 | 1.65 | 5.0207 | 12.033 | 5 | 12 | 82.2984 | 40 | -0.033046 | 5.342 | -0.0021585 | -0.45971 | 7.2275 | 0 | 6.7677 |  | 17.1677 | 4 | 17.1677 | 82.2984 | 41.1492 | 15 | 35 | 6.1492 | 113.7339 | 0.033046 | 0.001349 | 1 | 0
100 | 1.6667 | 5.022 | 12.0351 | 5 | 12 | 81.8201 | 40 | -0.03513 | 5.3069 | -0.0020842 | -0.48871 | 7.1799 | 0 | 6.6912 |  | 17.0912 | 4 | 17.0912 | 81.8201 | 40.9101 | 15 | 35 | 5.9101 | 119.6439 | 0.03513 | 0.0013026 | 1 | 0
101 | 1.6833 | 5.0232 | 12.0371 | 5 | 12 | 81.3315 | 40 | -0.037138 | 5.2698 | -0.0020079 | -0.51664 | 7.1297 | 0 | 6.613 |  | 17.013 | 4 | 17.013 | 81.3315 | 40.6658 | 15 | 35 | 5.6658 | 125.3097 | 0.037138 | 0.0012549 | 1 | 0
102 | 1.7 | 5.0244 | 12.0391 | 5 | 12 | 80.8334 | 40 | -0.039067 | 5.2307 | -0.0019298 | -0.54349 | 7.0768 | 0 | 6.5333 |  | 16.9333 | 4 | 16.9333 | 80.8334 | 40.4167 | 15 | 35 | 5.4167 | 130.7264 | 0.039067 | 0.0012061 | 1 | 0
103 | 1.7167 | 5.0256 | 12.0409 | 5 | 12 | 80.3265 | 40 | -0.040917 | 5.1898 | -0.00185 | -0.56923 | 7.0215 | 0 | 6.4522 |  | 16.8522 | 4 | 16.8522 | 80.3265 | 40.1633 | 15 | 35 | 5.1633 | 135.8897 | 0.040917 | 0.0011563 | 1 | 0
104 | 1.7333 | 5.0267 | 12.0427 | 5 | 12 | 79.8118 | 40 | -0.042686 | 5.1471 | -0.0017687 | -0.59383 | 6.9637 | 0 | 6.3699 |  | 16.7699 | 4 | 16.7699 | 79.8118 | 39.9059 | 15 | 35 | 4.9059 | 140.7956 | 0.042686 | 0.0011054 | 1 | 0
105 | 1.75 | 5.0277 | 12.0444 | 5 | 12 | 79.29 | 40 | -0.044372 | 5.1027 | -0.001686 | -0.61729 | 6.9037 | 0 | 6.2864 |  | 16.6864 | 4 | 16.6864 | 79.29 | 39.645 | 15 | 35 | 4.645 | 145.4406 | 0.044372 | 0.0010537 | 1 | 0
106 | 1.7667 | 5.0287 | 12.046 | 5 | 12 | 78.762 | 40 | -0.045974 | 5.0568 | -0.0016019 | -0.63957 | 6.8415 | 0 | 6.2019 |  | 16.6019 | 4 | 16.6019 | 78.762 | 39.381 | 15 | 35 | 4.381 | 149.8216 | 0.045974 | 0.0010012 | 1 | 0
107 | 1.7833 | 5.0297 | 12.0475 | 5 | 12 | 78.2285 | 40 | -0.047491 | 5.0093 | -0.0015167 | -0.66067 | 6.7772 | 0 | 6.1166 |  | 16.5166 | 4 | 16.5166 | 78.2285 | 39.1143 | 15 | 35 | 4.1143 | 153.9358 | 0.047491 | 0.00094796 | 1 | 0
108 | 1.8 | 5.0306 | 12.0489 | 5 | 12 | 77.6905 | 40 | -0.048921 | 4.9603 | -0.0014305 | -0.68057 | 6.711 | 0 | 6.0305 |  | 16.4305 | 4 | 16.4305 | 77.6905 | 38.8452 | 15 | 35 | 3.8452 | 157.781 | 0.048921 | 0.00089408 | 1 | 0
109 | 1.8167 | 5.0314 | 12.0503 | 5 | 12 | 77.1486 | 40 | -0.050265 | 4.9101 | -0.0013434 | -0.69926 | 6.643 | 0 | 5.9438 |  | 16.3438 | 4 | 16.3438 | 77.1486 | 38.5743 | 15 | 35 | 3.5743 | 161.3554 | 0.050265 | 0.00083964 | 1 | 0
110 | 1.8333 | 5.0322 | 12.0515 | 5 | 12 | 76.6038 | 40 | -0.05152 | 4.8586 | -0.0012556 | -0.71673 | 6.5733 | 0 | 5.8566 |  | 16.2566 | 4 | 16.2566 | 76.6038 | 38.3019 | 15 | 35 | 3.3019 | 164.6573 | 0.05152 | 0.00078474 | 1 | 0
111 | 1.85 | 5.0329 | 12.0527 | 5 | 12 | 76.0568 | 40 | -0.052687 | 4.8059 | -0.0011671 | -0.73296 | 6.5021 | 0 | 5.7691 |  | 16.1691 | 4 | 16.1691 | 76.0568 | 38.0284 | 15 | 35 | 3.0284 | 167.6857 | 0.052687 | 0.00072945 | 1 | 0
112 | 1.8667 | 5.0336 | 12.0538 | 5 | 12 | 75.5084 | 40 | -0.053766 | 4.7521 | -0.0010782 | -0.74796 | 6.4293 | 0 | 5.6813 |  | 16.0813 | 4 | 16.0813 | 75.5084 | 37.7542 | 15 | 35 | 2.7542 | 170.4399 | 0.053766 | 0.00067386 | 1 | 0
113 | 1.8833 | 5.0342 | 12.0548 | 5 | 12 | 74.9595 | 40 | -0.054755 | 4.6973 | -0.00098887 | -0.76172 | 6.3552 | 0 | 5.5935 |  | 15.9935 | 4 | 15.9935 | 74.9595 | 37.4797 | 15 | 35 | 2.4797 | 172.9196 | 0.054755 | 0.00061804 | 1 | 0
114 | 1.9 | 5.0348 | 12.0557 | 5 | 12 | 74.4107 | 40 | -0.055654 | 4.6417 | -0.00089934 | -0.77423 | 6.2799 | 0 | 5.5057 |  | 15.9057 | 4 | 15.9057 | 74.4107 | 37.2053 | 15 | 35 | 2.2053 | 175.1249 | 0.055654 | 0.00056208 | 1 | 0
115 | 1.9167 | 5.0353 | 12.0565 | 5 | 12 | 73.8628 | 40 | -0.056464 | 4.5852 | -0.00080971 | -0.7855 | 6.2035 | 0 | 5.418 |  | 15.818 | 4 | 15.818 | 73.8628 | 36.9314 | 15 | 35 | 1.9314 | 177.0563 | 0.056464 | 0.00050607 | 1 | 0
116 | 1.9333 | 5.0357 | 12.0572 | 5 | 12 | 73.3167 | 40 | -0.057184 | 4.528 | -0.00072011 | -0.79551 | 6.1262 | 0 | 5.3307 |  | 15.7307 | 4 | 15.7307 | 73.3167 | 36.6583 | 15 | 35 | 1.6583 | 178.7147 | 0.057184 | 0.00045007 | 1 | 0
117 | 1.95 | 5.0361 | 12.0578 | 5 | 12 | 72.7729 | 40 | -0.057814 | 4.4702 | -0.00063066 | -0.80429 | 6.048 | 0 | 5.2437 |  | 15.6437 | 4 | 15.6437 | 72.7729 | 36.3865 | 15 | 35 | 1.3865 | 180.1011 | 0.057814 | 0.00039416 | 1 | 0
118 | 1.9667 | 5.0365 | 12.0584 | 5 | 12 | 72.2324 | 40 | -0.058356 | 4.4119 | -0.00054149 | -0.81182 | 5.969 | 0 | 5.1572 |  | 15.5572 | 4 | 15.5572 | 72.2324 | 36.1162 | 15 | 35 | 1.1162 | 181.2173 | 0.058356 | 0.00033843 | 1 | 0
119 | 1.9833 | 5.0368 | 12.0588 | 5 | 12 | 71.6958 | 40 | -0.058809 | 4.3531 | -0.00045273 | -0.81812 | 5.8894 | 0 | 5.0713 |  | 15.4713 | 4 | 15.4713 | 71.6958 | 35.8479 | 15 | 35 | 0.84789 | 182.0652 | 0.058809 | 0.00028295 | 1 | 0
120 | 2 | 5.037 | 12.0592 | 5 | 12 | 71.1637 | 40 | -0.059173 | 4.2939 | -0.00036448 | -0.82319 | 5.8094 | 0 | 4.9862 |  | 15.3862 | 4 | 15.3862 | 71.1637 | 35.5819 | 15 | 35 | 0.58186 | 182.6471 | 0.059173 | 0.0002278 | 1 | 0
121 | 2.0167 | 5.0372 | 12.0594 | 5 | 12 | 70.637 | 40 | -0.05945 | 4.2344 | -0.00027686 | -0.82704 | 5.729 | 0 | 4.9019 |  | 15.3019 | 4 | 15.3019 | 70.637 | 35.3185 | 15 | 35 | 0.31848 | 182.9656 | 0.05945 | 0.00017304 | 1 | 0
122 | 2.0333 | 5.0373 | 12.0596 | 5 | 12 | 70.1161 | 40 | -0.05964 | 4.1748 | -0.00019 | -0.82968 | 5.6483 | 0 | 4.8186 |  | 15.2186 | 4 | 15.2186 | 70.1161 | 35.0581 | 15 | 35 | 0.058062 | 183.0236 | 0.05964 | 0.00011875 | 1 | 0
123 | 2.05 | 5.0373 | 12.0597 | 5 | 12 | 69.6019 | 40 | -0.059744 | 4.1151 | -0.00010399 | -0.83113 | 5.5674 | 0 | 4.7363 |  | 15.1363 | 4 | 15.1363 | 69.6019 | 34.8009 | 15 | 35 | -0.19905 | 182.8246 | 0.059744 | 6.4995e-05 | 1 | 0
124 | 2.0667 | 5.0374 | 12.0598 | 5 | 12 | 69.0949 | 40 | -0.059763 | 4.0553 | -1.8959e-05 | -0.83139 | 5.4866 | 0 | 4.6552 |  | 15.0552 | 4 | 15.0552 | 69.0949 | 34.5474 | 15 | 35 | -0.45255 | 182.372 | 0.059763 | 1.1849e-05 | 1 | 0
125 | 2.0833 | 5.0373 | 12.0597 | 5 | 12 | 68.5958 | 40 | -0.059698 | 3.9956 | 6.4997e-05 | -0.83049 | 5.4058 | 0 | 4.5753 |  | 14.9753 | 4 | 14.9753 | 68.5958 | 34.2979 | 15 | 35 | -0.70212 | 181.6699 | 0.059698 | -4.0623e-05 | -1 | -2
126 | 2.1 | 5.0372 | 12.0596 | 5 | 12 | 68.1051 | 40 | -0.05955 | 3.936 | 0.00014777 | -0.82843 | 5.3252 | 0 | 4.4968 |  | 14.8968 | 4 | 14.8968 | 68.1051 | 34.0525 | 15 | 35 | -0.94747 | 180.7224 | 0.05955 | -9.2357e-05 | -1 | 0
127 | 2.1167 | 5.0371 | 12.0593 | 5 | 12 | 67.6234 | 40 | -0.059321 | 3.8767 | 0.00022926 | -0.82524 | 5.245 | 0 | 4.4197 |  | 14.8197 | 4 | 14.8197 | 67.6234 | 33.8117 | 15 | 35 | -1.1883 | 179.5341 | 0.059321 | -0.00014329 | -1 | 0
128 | 2.1333 | 5.0369 | 12.059 | 5 | 12 | 67.1513 | 40 | -0.059011 | 3.8177 | 0.00030938 | -0.82094 | 5.1651 | 0 | 4.3442 |  | 14.7442 | 4 | 14.7442 | 67.1513 | 33.5756 | 15 | 35 | -1.4244 | 178.1098 | 0.059011 | -0.00019336 | -1 | 0
129 | 2.15 | 5.0366 | 12.0586 | 5 | 12 | 66.6893 | 40 | -0.058623 | 3.7591 | 0.00038802 | -0.81554 | 5.0858 | 0 | 4.2703 |  | 14.6703 | 4 | 14.6703 | 66.6893 | 33.3447 | 15 | 35 | -1.6553 | 176.4544 | 0.058623 | -0.00024251 | -1 | 0
130 | 2.1667 | 5.0363 | 12.0582 | 5 | 12 | 66.238 | 40 | -0.058158 | 3.7009 | 0.0004651 | -0.80907 | 5.0071 | 0 | 4.1981 |  | 14.5981 | 4 | 14.5981 | 66.238 | 33.119 | 15 | 35 | -1.881 | 174.5734 | 0.058158 | -0.00029069 | -1 | 0
131 | 2.1833 | 5.036 | 12.0576 | 5 | 12 | 65.7978 | 40 | -0.057618 | 3.6433 | 0.00054052 | -0.80155 | 4.9292 | 0 | 4.1276 |  | 14.5276 | 4 | 14.5276 | 65.7978 | 32.8989 | 15 | 35 | -2.1011 | 172.4723 | 0.057618 | -0.00033783 | -1 | 0
132 | 2.2 | 5.0356 | 12.057 | 5 | 12 | 65.3691 | 40 | -0.057004 | 3.5863 | 0.00061421 | -0.79301 | 4.8521 | 0 | 4.0591 |  | 14.4591 | 4 | 14.4591 | 65.3691 | 32.6846 | 15 | 35 | -2.3154 | 170.1569 | 0.057004 | -0.00038388 | -1 | 0
133 | 2.2167 | 5.0352 | 12.0563 | 5 | 12 | 64.9526 | 40 | -0.056317 | 3.53 | 0.00068608 | -0.78346 | 4.7759 | 0 | 3.9924 |  | 14.3924 | 4 | 14.3924 | 64.9526 | 32.4763 | 15 | 35 | -2.5237 | 167.6331 | 0.056317 | -0.0004288 | -1 | 0
134 | 2.2333 | 5.0347 | 12.0556 | 5 | 12 | 64.5485 | 40 | -0.055561 | 3.4744 | 0.00075606 | -0.77295 | 4.7007 | 0 | 3.9278 |  | 14.3278 | 4 | 14.3278 | 64.5485 | 32.2742 | 15 | 35 | -2.7258 | 164.9074 | 0.055561 | -0.00047254 | -1 | 0
135 | 2.25 | 5.0342 | 12.0547 | 5 | 12 | 64.1573 | 40 | -0.054737 | 3.4197 | 0.00082407 | -0.76148 | 4.6266 | 0 | 3.8652 |  | 14.2652 | 4 | 14.2652 | 64.1573 | 32.0786 | 15 | 35 | -2.9214 | 161.986 | 0.054737 | -0.00051504 | -1 | 0
136 | 2.2667 | 5.0337 | 12.0538 | 5 | 12 | 63.7794 | 40 | -0.053847 | 3.3658 | 0.00089004 | -0.7491 | 4.5538 | 0 | 3.8047 |  | 14.2047 | 4 | 14.2047 | 63.7794 | 31.8897 | 15 | 35 | -3.1103 | 158.8757 | 0.053847 | -0.00055628 | -1 | 0
137 | 2.2833 | 5.0331 | 12.0529 | 5 | 12 | 63.415 | 40 | -0.052893 | 3.313 | 0.00095391 | -0.73583 | 4.4822 | 0 | 3.7464 |  | 14.1464 | 4 | 14.1464 | 63.415 | 31.7075 | 15 | 35 | -3.2925 | 155.5832 | 0.052893 | -0.00059619 | -1 | 0
138 | 2.3 | 5.0324 | 12.0519 | 5 | 12 | 63.0647 | 40 | -0.051878 | 3.2611 | 0.0010156 | -0.7217 | 4.412 | 0 | 3.6903 |  | 14.0903 | 4 | 14.0903 | 63.0647 | 31.5323 | 15 | 35 | -3.4677 | 152.1156 | 0.051878 | -0.00063476 | -1 | 0
139 | 2.3167 | 5.0318 | 12.0508 | 5 | 12 | 62.7286 | 40 | -0.050803 | 3.2103 | 0.0010751 | -0.70674 | 4.3433 | 0 | 3.6366 |  | 14.0366 | 4 | 14.0366 | 62.7286 | 31.3643 | 15 | 35 | -3.6357 | 148.4799 | 0.050803 | -0.00067194 | -1 | 0
140 | 2.3333 | 5.031 | 12.0497 | 5 | 12 | 62.407 | 40 | -0.04967 | 3.1606 | 0.0011323 | -0.69099 | 4.2761 | 0 | 3.5851 |  | 13.9851 | 4 | 13.9851 | 62.407 | 31.2035 | 15 | 35 | -3.7965 | 144.6834 | 0.04967 | -0.00070769 | -1 | 0
141 | 2.35 | 5.0303 | 12.0485 | 5 | 12 | 62.1003 | 40 | -0.048483 | 3.1121 | 0.0011872 | -0.67448 | 4.2105 | 0 | 3.536 |  | 13.936 | 4 | 13.936 | 62.1003 | 31.0501 | 15 | 35 | -3.9499 | 140.7335 | 0.048483 | -0.00074198 | -1 | 0
142 | 2.3667 | 5.0295 | 12.0472 | 5 | 12 | 61.8086 | 40 | -0.047244 | 3.0649 | 0.0012397 | -0.65723 | 4.1466 | 0 | 3.4894 |  | 13.8894 | 4 | 13.8894 | 61.8086 | 30.9043 | 15 | 35 | -4.0957 | 136.6378 | 0.047244 | -0.0007748 | -1 | 0
143 | 2.3833 | 5.0287 | 12.046 | 5 | 12 | 61.5321 | 40 | -0.045954 | 3.0189 | 0.0012898 | -0.63929 | 4.0844 | 0 | 3.4451 |  | 13.8451 | 4 | 13.8451 | 61.5321 | 30.7661 | 15 | 35 | -4.2339 | 132.4038 | 0.045954 | -0.0008061 | -1 | 0
144 | 2.4 | 5.0279 | 12.0446 | 5 | 12 | 61.2711 | 40 | -0.044616 | 2.9743 | 0.0013374 | -0.62068 | 4.0241 | 0 | 3.4034 |  | 13.8034 | 4 | 13.8034 | 61.2711 | 30.6356 | 15 | 35 | -4.3644 | 128.0394 | 0.044616 | -0.00083586 | -1 | 0
145 | 2.4167 | 5.027 | 12.0432 | 5 | 12 | 61.0258 | 40 | -0.043234 | 2.9311 | 0.0013825 | -0.60145 | 3.9656 | 0 | 3.3641 |  | 13.7641 | 4 | 13.7641 | 61.0258 | 30.5129 | 15 | 35 | -4.4871 | 123.5523 | 0.043234 | -0.00086407 | -1 | 0
146 | 2.4333 | 5.0261 | 12.0418 | 5 | 12 | 60.7961 | 40 | -0.041809 | 2.8893 | 0.0014251 | -0.58163 | 3.909 | 0 | 3.3274 |  | 13.7274 | 4 | 13.7274 | 60.7961 | 30.3981 | 15 | 35 | -4.6019 | 118.9503 | 0.041809 | -0.0008907 | -1 | 0
147 | 2.45 | 5.0252 | 12.0403 | 5 | 12 | 60.5824 | 40 | -0.040344 | 2.8489 | 0.0014652 | -0.56124 | 3.8544 | 0 | 3.2932 |  | 13.6932 | 4 | 13.6932 | 60.5824 | 30.2912 | 15 | 35 | -4.7088 | 114.2415 | 0.040344 | -0.00091574 | -1 | 0
148 | 2.4667 | 5.0243 | 12.0388 | 5 | 12 | 60.3846 | 40 | -0.038841 | 2.8101 | 0.0015027 | -0.54034 | 3.8019 | 0 | 3.2615 |  | 13.6615 | 4 | 13.6615 | 60.3846 | 30.1923 | 15 | 35 | -4.8077 | 109.4338 | 0.038841 | -0.00093917 | -1 | 0
149 | 2.4833 | 5.0233 | 12.0373 | 5 | 12 | 60.2029 | 40 | -0.037303 | 2.7728 | 0.0015376 | -0.51895 | 3.7514 | 0 | 3.2325 |  | 13.6325 | 4 | 13.6325 | 60.2029 | 30.1014 | 15 | 35 | -4.8986 | 104.5353 | 0.037303 | -0.00096098 | -1 | 0
150 | 2.5 | 5.0223 | 12.0357 | 5 | 12 | 60.0372 | 40 | -0.035733 | 2.737 | 0.0015699 | -0.49711 | 3.7031 | 0 | 3.206 |  | 13.606 | 4 | 13.606 | 60.0372 | 30.0186 | 15 | 35 | -4.9814 | 99.5539 | 0.035733 | -0.00098116 | -1 | 0
151 | 2.5167 | 5.0213 | 12.0341 | 5 | 12 | 59.8876 | 40 | -0.034134 | 2.7029 | 0.0015995 | -0.47486 | 3.6569 | 0 | 3.182 |  | 13.582 | 4 | 13.582 | 59.8876 | 29.9438 | 15 | 35 | -5.0562 | 94.4977 | 0.034134 | -0.00099971 | -1 | 0
152 | 2.5333 | 5.0203 | 12.0325 | 5 | 12 | 59.7542 | 40 | -0.032507 | 2.6704 | 0.0016266 | -0.45223 | 3.6129 | 0 | 3.1607 |  | 13.5607 | 4 | 13.5607 | 59.7542 | 29.8771 | 15 | 35 | -5.1229 | 89.3748 | 0.032507 | -0.0010166 | -1 | 0
153 | 2.55 | 5.0193 | 12.0309 | 5 | 12 | 59.6368 | 40 | -0.030856 | 2.6395 | 0.001651 | -0.42926 | 3.5712 | 0 | 3.1419 |  | 13.5419 | 4 | 13.5419 | 59.6368 | 29.8184 | 15 | 35 | -5.1816 | 84.1932 | 0.030856 | -0.0010319 | -1 | 0
154 | 2.5667 | 5.0182 | 12.0292 | 5 | 12 | 59.5355 | 40 | -0.029184 | 2.6104 | 0.0016728 | -0.40599 | 3.5317 | 0 | 3.1257 |  | 13.5257 | 4 | 13.5257 | 59.5355 | 29.7677 | 15 | 35 | -5.2323 | 78.9609 | 0.029184 | -0.0010455 | -1 | 0
155 | 2.5833 | 5.0172 | 12.0275 | 5 | 12 | 59.4501 | 40 | -0.027492 | 2.5829 | 0.0016919 | -0.38245 | 3.4945 | 0 | 3.112 |  | 13.512 | 4 | 13.512 | 59.4501 | 29.7251 | 15 | 35 | -5.2749 | 73.686 | 0.027492 | -0.0010575 | -1 | 0
156 | 2.6 | 5.0161 | 12.0258 | 5 | 12 | 59.3807 | 40 | -0.025783 | 2.5571 | 0.0017085 | -0.35868 | 3.4596 | 0 | 3.1009 |  | 13.5009 | 4 | 13.5009 | 59.3807 | 29.6903 | 15 | 35 | -5.3097 | 68.3763 | 0.025783 | -0.0010678 | -1 | 0
157 | 2.6167 | 5.015 | 12.0241 | 5 | 12 | 59.327 | 40 | -0.024061 | 2.533 | 0.0017224 | -0.33472 | 3.427 | 0 | 3.0923 |  | 13.4923 | 4 | 13.4923 | 59.327 | 29.6635 | 15 | 35 | -5.3365 | 63.0398 | 0.024061 | -0.0010765 | -1 | 0
158 | 2.6333 | 5.014 | 12.0223 | 5 | 12 | 59.2889 | 40 | -0.022327 | 2.5107 | 0.0017338 | -0.3106 | 3.3968 | 0 | 3.0862 |  | 13.4862 | 4 | 13.4862 | 59.2889 | 29.6445 | 15 | 35 | -5.3555 | 57.6843 | 0.022327 | -0.0010836 | -1 | 0
159 | 2.65 | 5.0129 | 12.0206 | 5 | 12 | 59.2664 | 40 | -0.020584 | 2.4901 | 0.0017425 | -0.28636 | 3.369 | 0 | 3.0826 |  | 13.4826 | 4 | 13.4826 | 59.2664 | 29.6332 | 15 | 35 | -5.3668 | 52.3175 | 0.020584 | -0.0010891 | -1 | 0
160 | 2.6667 | 5.0118 | 12.0188 | 5 | 12 | 59.2591 | 40 | -0.018836 | 2.4713 | 0.0017487 | -0.26203 | 3.3435 | 0 | 3.0815 |  | 13.4815 | 4 | 13.4815 | 59.2591 | 29.6296 | 15 | 35 | -5.3704 | 46.947 | 0.018836 | -0.001093 | -1 | 0
161 | 2.6833 | 5.0107 | 12.0171 | 5 | 12 | 59.2671 | 40 | -0.017083 | 2.4542 | 0.0017524 | -0.23765 | 3.3204 | 0 | 3.0827 |  | 13.4827 | 4 | 13.4827 | 59.2671 | 29.6335 | 15 | 35 | -5.3665 | 41.5806 | 0.017083 | -0.0010953 | -1 | 0
162 | 2.7 | 5.0096 | 12.0153 | 5 | 12 | 59.2899 | 40 | -0.01533 | 2.4389 | 0.0017536 | -0.21326 | 3.2996 | 0 | 3.0864 |  | 13.4864 | 4 | 13.4864 | 59.2899 | 29.645 | 15 | 35 | -5.355 | 36.2255 | 0.01533 | -0.001096 | -1 | 0
163 | 2.7167 | 5.0085 | 12.0136 | 5 | 12 | 59.3275 | 40 | -0.013577 | 2.4253 | 0.0017523 | -0.18888 | 3.2813 | 0 | 3.0924 |  | 13.4924 | 4 | 13.4924 | 59.3275 | 29.6637 | 15 | 35 | -5.3363 | 30.8893 | 0.013577 | -0.0010952 | -1 | 0
164 | 2.7333 | 5.0074 | 12.0118 | 5 | 12 | 59.3795 | 40 | -0.011829 | 2.4135 | 0.0017486 | -0.16456 | 3.2653 | 0 | 3.1007 |  | 13.5007 | 4 | 13.5007 | 59.3795 | 29.6897 | 15 | 35 | -5.3103 | 25.579 | 0.011829 | -0.0010929 | -1 | 0
165 | 2.75 | 5.0063 | 12.0101 | 5 | 12 | 59.4457 | 40 | -0.010086 | 2.4034 | 0.0017425 | -0.14032 | 3.2516 | 0 | 3.1113 |  | 13.5113 | 4 | 13.5113 | 59.4457 | 29.7228 | 15 | 35 | -5.2772 | 20.3018 | 0.010086 | -0.001089 | -1 | 0
166 | 2.7667 | 5.0052 | 12.0084 | 5 | 12 | 59.5258 | 40 | -0.0083523 | 2.395 | 0.001734 | -0.11619 | 3.2403 | 0 | 3.1241 |  | 13.5241 | 4 | 13.5241 | 59.5258 | 29.7629 | 15 | 35 | -5.2371 | 15.0648 | 0.0083523 | -0.0010837 | -1 | 0
167 | 2.7833 | 5.0041 | 12.0066 | 5 | 12 | 59.6196 | 40 | -0.0066292 | 2.3884 | 0.0017232 | -0.092222 | 3.2314 | 0 | 3.1391 |  | 13.5391 | 4 | 13.5391 | 59.6196 | 29.8098 | 15 | 35 | -5.1902 | 9.8745 | 0.0066292 | -0.001077 | -1 | 0
168 | 2.8 | 5.0031 | 12.0049 | 5 | 12 | 59.7267 | 40 | -0.0049191 | 2.3835 | 0.0017101 | -0.068432 | 3.2247 | 0 | 3.1563 |  | 13.5563 | 4 | 13.5563 | 59.7267 | 29.8633 | 15 | 35 | -5.1367 | 4.7379 | 0.0049191 | -0.0010688 | -1 | 0
169 | 2.8167 | 5.002 | 12.0032 | 5 | 12 | 59.8468 | 40 | -0.0032243 | 2.3803 | 0.0016948 | -0.044856 | 3.2203 | 0 | 3.1755 |  | 13.5755 | 4 | 13.5755 | 59.8468 | 29.9234 | 15 | 35 | -5.0766 | -0.33873 | 0.0032243 | -0.0010592 | -1 | 0
170 | 2.8333 | 5.001 | 12.0015 | 5 | 12 | 59.9795 | 40 | -0.0015471 | 2.3787 | 0.0016773 | -0.021522 | 3.2182 | 0 | 3.1967 |  | 13.5967 | 4 | 13.5967 | 59.9795 | 29.9898 | 15 | 35 | -5.0102 | -5.349 | 0.0015471 | -0.0010483 | -1 | 0
171 | 2.85 | 4.9999 | 11.9999 | 5 | 12 | 60.1246 | 40 | 0.0001106 | 2.3788 | 0.0016577 | 0.0015387 | 3.2184 | 0 | 3.2199 |  | 13.6199 | 4 | 13.6199 | 60.1246 | 30.0623 | 15 | 35 | -4.9377 | -10.2867 | 0.0001106 | -0.001036 | -1 | 0
172 | 2.8667 | 4.9989 | 11.9983 | 5 | 12 | 60.2816 | 40 | 0.0017466 | 2.3806 | 0.001636 | 0.024298 | 3.2208 | 0 | 3.2451 |  | 13.6451 | 4 | 13.6451 | 60.2816 | 30.1408 | 15 | 35 | -4.8592 | -15.1459 | 0.0017466 | -0.0010225 | -1 | 0
173 | 2.8833 | 4.9979 | 11.9966 | 5 | 12 | 60.4502 | 40 | 0.0033589 | 2.3839 | 0.0016123 | 0.046728 | 3.2253 | 0 | 3.272 |  | 13.672 | 4 | 13.672 | 60.4502 | 30.2251 | 15 | 35 | -4.7749 | -19.9208 | 0.0033589 | -0.0010077 | -1 | 0
174 | 2.9 | 4.9969 | 11.9951 | 5 | 12 | 60.63 | 40 | 0.0049456 | 2.3889 | 0.0015867 | 0.068801 | 3.232 | 0 | 3.3008 |  | 13.7008 | 4 | 13.7008 | 60.63 | 30.315 | 15 | 35 | -4.685 | -24.6058 | 0.0049456 | -0.00099167 | -1 | 0
175 | 2.9167 | 4.9959 | 11.9935 | 5 | 12 | 60.8205 | 40 | 0.0065047 | 2.3954 | 0.0015592 | 0.090491 | 3.2408 | 0 | 3.3313 |  | 13.7313 | 4 | 13.7313 | 60.8205 | 30.4103 | 15 | 35 | -4.5897 | -29.1955 | 0.0065047 | -0.00097447 | -1 | 0
176 | 2.9333 | 4.995 | 11.992 | 5 | 12 | 61.0215 | 40 | 0.0080345 | 2.4034 | 0.0015298 | 0.11177 | 3.2517 | 0 | 3.3634 |  | 13.7634 | 4 | 13.7634 | 61.0215 | 30.5107 | 15 | 35 | -4.4893 | -33.6848 | 0.0080345 | -0.00095613 | -1 | 0
177 | 2.95 | 4.994 | 11.9905 | 5 | 12 | 61.2324 | 40 | 0.0095332 | 2.4129 | 0.0014987 | 0.13262 | 3.2646 | 0 | 3.3972 |  | 13.7972 | 4 | 13.7972 | 61.2324 | 30.6162 | 15 | 35 | -4.3838 | -38.0686 | 0.0095332 | -0.00093668 | -1 | 0
178 | 2.9667 | 4.9931 | 11.989 | 5 | 12 | 61.4529 | 40 | 0.010999 | 2.4239 | 0.0014659 | 0.15301 | 3.2794 | 0 | 3.4325 |  | 13.8325 | 4 | 13.8325 | 61.4529 | 30.7264 | 15 | 35 | -4.2736 | -42.3421 | 0.010999 | -0.00091617 | -1 | 0
179 | 2.9833 | 4.9922 | 11.9876 | 5 | 12 | 61.6824 | 40 | 0.012431 | 2.4364 | 0.0014314 | 0.17293 | 3.2963 | 0 | 3.4692 |  | 13.8692 | 4 | 13.8692 | 61.6824 | 30.8412 | 15 | 35 | -4.1588 | -46.5009 | 0.012431 | -0.00089465 | -1 | 0
180 | 3 | 4.9914 | 11.9862 | 5 | 12 | 61.9207 | 40 | 0.013826 | 2.4502 | 0.0013955 | 0.19234 | 3.315 | 0 | 3.5073 |  | 13.9073 | 4 | 13.9073 | 61.9207 | 30.9603 | 15 | 35 | -4.0397 | -50.5406 | 0.013826 | -0.00087216 | -1 | 0
181 | 3.0167 | 4.9905 | 11.9848 | 5 | 12 | 62.1671 | 40 | 0.015184 | 2.4654 | 0.001358 | 0.21123 | 3.3355 | 0 | 3.5467 |  | 13.9467 | 4 | 13.9467 | 62.1671 | 31.0836 | 15 | 35 | -3.9164 | -54.457 | 0.015184 | -0.00084873 | -1 | 0
182 | 3.0333 | 4.9897 | 11.9835 | 5 | 12 | 62.4214 | 40 | 0.016503 | 2.4819 | 0.0013191 | 0.22958 | 3.3578 | 0 | 3.5874 |  | 13.9874 | 4 | 13.9874 | 62.4214 | 31.2107 | 15 | 35 | -3.7893 | -58.2463 | 0.016503 | -0.00082442 | -1 | 0
183 | 3.05 | 4.9889 | 11.9822 | 5 | 12 | 62.6829 | 40 | 0.017782 | 2.4997 | 0.0012788 | 0.24737 | 3.3819 | 0 | 3.6293 |  | 14.0293 | 4 | 14.0293 | 62.6829 | 31.3415 | 15 | 35 | -3.6585 | -61.9049 | 0.017782 | -0.00079927 | -1 | 0
184 | 3.0667 | 4.9881 | 11.981 | 5 | 12 | 62.9513 | 40 | 0.019019 | 2.5187 | 0.0012373 | 0.26459 | 3.4076 | 0 | 3.6722 |  | 14.0722 | 4 | 14.0722 | 62.9513 | 31.4757 | 15 | 35 | -3.5243 | -65.4292 | 0.019019 | -0.00077333 | -1 | 0
185 | 3.0833 | 4.9874 | 11.9798 | 5 | 12 | 63.2261 | 40 | 0.020214 | 2.5389 | 0.0011946 | 0.28121 | 3.435 | 0 | 3.7162 |  | 14.1162 | 4 | 14.1162 | 63.2261 | 31.6131 | 15 | 35 | -3.3869 | -68.8161 | 0.020214 | -0.00074664 | -1 | 0
186 | 3.1 | 4.9866 | 11.9786 | 5 | 12 | 63.5069 | 40 | 0.021365 | 2.5603 | 0.0011508 | 0.29722 | 3.4639 | 0 | 3.7611 |  | 14.1611 | 4 | 14.1611 | 63.5069 | 31.7534 | 15 | 35 | -3.2466 | -72.0627 | 0.021365 | -0.00071925 | -1 | 0
187 | 3.1167 | 4.986 | 11.9775 | 5 | 12 | 63.793 | 40 | 0.022471 | 2.5827 | 0.0011059 | 0.3126 | 3.4943 | 0 | 3.8069 |  | 14.2069 | 4 | 14.2069 | 63.793 | 31.8965 | 15 | 35 | -3.1035 | -75.1662 | 0.022471 | -0.00069121 | -1 | 0
188 | 3.1333 | 4.9853 | 11.9765 | 5 | 12 | 64.0842 | 40 | 0.023531 | 2.6063 | 0.0010601 | 0.32735 | 3.5261 | 0 | 3.8535 |  | 14.2535 | 4 | 14.2535 | 64.0842 | 32.0421 | 15 | 35 | -2.9579 | -78.1241 | 0.023531 | -0.00066257 | -1 | 0
189 | 3.15 | 4.9847 | 11.9755 | 5 | 12 | 64.3798 | 40 | 0.024544 | 2.6308 | 0.0010134 | 0.34145 | 3.5593 | 0 | 3.9008 |  | 14.3008 | 4 | 14.3008 | 64.3798 | 32.1899 | 15 | 35 | -2.8101 | -80.9342 | 0.024544 | -0.00063337 | -1 | 0
190 | 3.1667 | 4.9841 | 11.9745 | 5 | 12 | 64.6795 | 40 | 0.02551 | 2.6563 | 0.00096585 | 0.35488 | 3.5938 | 0 | 3.9487 |  | 14.3487 | 4 | 14.3487 | 64.6795 | 32.3398 | 15 | 35 | -2.6602 | -83.5944 | 0.02551 | -0.00060366 | -1 | 0
191 | 3.1833 | 4.9835 | 11.9736 | 5 | 12 | 64.9828 | 40 | 0.026427 | 2.6827 | 0.00091758 | 0.36765 | 3.6296 | 0 | 3.9972 |  | 14.3972 | 4 | 14.3972 | 64.9828 | 32.4914 | 15 | 35 | -2.5086 | -86.1031 | 0.026427 | -0.00057349 | -1 | 0
192 | 3.2 | 4.9829 | 11.9727 | 5 | 12 | 65.2891 | 40 | 0.027296 | 2.71 | 0.00086865 | 0.37973 | 3.6665 | 0 | 4.0463 |  | 14.4463 | 4 | 14.4463 | 65.2891 | 32.6445 | 15 | 35 | -2.3555 | -88.4585 | 0.027296 | -0.00054291 | -1 | 0
193 | 3.2167 | 4.9824 | 11.9719 | 5 | 12 | 65.5981 | 40 | 0.028115 | 2.7382 | 0.00081914 | 0.39113 | 3.7046 | 0 | 4.0957 |  | 14.4957 | 4 | 14.4957 | 65.5981 | 32.799 | 15 | 35 | -2.201 | -90.6595 | 0.028115 | -0.00051196 | -1 | 0
194 | 3.2333 | 4.9819 | 11.9711 | 5 | 12 | 65.9092 | 40 | 0.028884 | 2.767 | 0.00076913 | 0.40183 | 3.7436 | 0 | 4.1455 |  | 14.5455 | 4 | 14.5455 | 65.9092 | 32.9546 | 15 | 35 | -2.0454 | -92.7049 | 0.028884 | -0.0004807 | -1 | 0
195 | 3.25 | 4.9815 | 11.9704 | 5 | 12 | 66.222 | 40 | 0.029603 | 2.7966 | 0.00071868 | 0.41183 | 3.7837 | 0 | 4.1955 |  | 14.5955 | 4 | 14.5955 | 66.222 | 33.111 | 15 | 35 | -1.889 | -94.5939 | 0.029603 | -0.00044918 | -1 | 0
196 | 3.2667 | 4.9811 | 11.9697 | 5 | 12 | 66.536 | 40 | 0.030271 | 2.8269 | 0.00066789 | 0.42112 | 3.8246 | 0 | 4.2458 |  | 14.6458 | 4 | 14.6458 | 66.536 | 33.268 | 15 | 35 | -1.732 | -96.3259 | 0.030271 | -0.00041743 | -1 | 0
197 | 3.2833 | 4.9807 | 11.9691 | 5 | 12 | 66.8508 | 40 | 0.030888 | 2.8578 | 0.00061682 | 0.4297 | 3.8664 | 0 | 4.2961 |  | 14.6961 | 4 | 14.6961 | 66.8508 | 33.4254 | 15 | 35 | -1.5746 | -97.9005 | 0.030888 | -0.00038551 | -1 | 0
198 | 3.3 | 4.9803 | 11.9685 | 5 | 12 | 67.166 | 40 | 0.031453 | 2.8893 | 0.00056555 | 0.43757 | 3.909 | 0 | 4.3466 |  | 14.7466 | 4 | 14.7466 | 67.166 | 33.583 | 15 | 35 | -1.417 | -99.3175 | 0.031453 | -0.00035347 | -1 | 0
199 | 3.3167 | 4.98 | 11.968 | 5 | 12 | 67.481 | 40 | 0.031968 | 2.9212 | 0.00051415 | 0.44472 | 3.9522 | 0 | 4.397 |  | 14.797 | 4 | 14.797 | 67.481 | 33.7405 | 15 | 35 | -1.2595 | -100.577 | 0.031968 | -0.00032134 | -1 | 0
200 | 3.3333 | 4.9797 | 11.9676 | 5 | 12 | 67.7954 | 40 | 0.03243 | 2.9537 | 0.0004627 | 0.45115 | 3.9961 | 0 | 4.4473 |  | 14.8473 | 4 | 14.8473 | 67.7954 | 33.8977 | 15 | 35 | -1.1023 | -101.6793 | 0.03243 | -0.00028919 | -1 | 0
201 | 3.35 | 4.9795 | 11.9672 | 5 | 12 | 68.1089 | 40 | 0.032841 | 2.9865 | 0.00041127 | 0.45688 | 4.0405 | 0 | 4.4974 |  | 14.8974 | 4 | 14.8974 | 68.1089 | 34.0545 | 15 | 35 | -0.94555 | -102.6248 | 0.032841 | -0.00025704 | -1 | 0
202 | 3.3667 | 4.9792 | 11.9668 | 5 | 12 | 68.4209 | 40 | 0.033201 | 3.0197 | 0.00035993 | 0.46188 | 4.0855 | 0 | 4.5474 |  | 14.9474 | 4 | 14.9474 | 68.4209 | 34.2105 | 15 | 35 | -0.78953 | -103.4144 | 0.033201 | -0.00022495 | -1 | 0
203 | 3.3833 | 4.9791 | 11.9665 | 5 | 12 | 68.7312 | 40 | 0.03351 | 3.0532 | 0.00030875 | 0.46618 | 4.1308 | 0 | 4.597 |  | 14.997 | 4 | 14.997 | 68.7312 | 34.3656 | 15 | 35 | -0.63442 | -104.0488 | 0.03351 | -0.00019297 | -1 | 0
204 | 3.4 | 4.9789 | 11.9662 | 5 | 12 | 69.0391 | 40 | 0.033768 | 3.087 | 0.0002578 | 0.46976 | 4.1765 | 0 | 4.6463 |  | 15.0463 | 4 | 15.0463 | 69.0391 | 34.5196 | 15 | 35 | -0.48045 | -104.5292 | 0.033768 | -0.00016113 | -1 | 0
205 | 3.4167 | 4.9788 | 11.966 | 5 | 12 | 69.3444 | 40 | 0.033975 | 3.1209 | 0.00020716 | 0.47265 | 4.2225 | 0 | 4.6951 |  | 15.0951 | 4 | 15.0951 | 69.3444 | 34.6722 | 15 | 35 | -0.3278 | -104.857 | 0.033975 | -0.00012947 | -1 | 0
206 | 3.4333 | 4.9787 | 11.9659 | 5 | 12 | 69.6467 | 40 | 0.034132 | 3.1551 | 0.00015688 | 0.47483 | 4.2686 | 0 | 4.7435 |  | 15.1435 | 4 | 15.1435 | 69.6467 | 34.8233 | 15 | 35 | -0.17667 | -105.0337 | 0.034132 | -9.8051e-05 | -1 | 0
207 | 3.45 | 4.9786 | 11.9658 | 5 | 12 | 69.9455 | 40 | 0.034239 | 3.1893 | 0.00010704 | 0.47632 | 4.315 | 0 | 4.7913 |  | 15.1913 | 4 | 15.1913 | 69.9455 | 34.9727 | 15 | 35 | -0.027255 | -105.0609 | 0.034239 | -6.6897e-05 | -1 | 0
208 | 3.4667 | 4.9786 | 11.9657 | 5 | 12 | 70.2405 | 40 | 0.034297 | 3.2236 | 5.7688e-05 | 0.47712 | 4.3614 | 0 | 4.8385 |  | 15.2385 | 4 | 15.2385 | 70.2405 | 35.1203 | 15 | 35 | 0.12026 | -104.9407 | 0.034297 | -3.6055e-05 | -1 | 0
209 | 3.4833 | 4.9786 | 11.9657 | 5 | 12 | 70.5314 | 40 | 0.034306 | 3.2579 | 8.8995e-06 | 0.47724 | 4.4078 | 0 | 4.885 |  | 15.285 | 4 | 15.285 | 70.5314 | 35.2657 | 15 | 35 | 0.26569 | -104.675 | 0.034306 | -5.5622e-06 | -1 | 0
210 | 3.5 | 4.9786 | 11.9657 | 5 | 12 | 70.8177 | 40 | 0.034266 | 3.2922 | -3.9268e-05 | 0.4767 | 4.4541 | 0 | 4.9308 |  | 15.3308 | 4 | 15.3308 | 70.8177 | 35.4089 | 15 | 35 | 0.40886 | -104.2661 | 0.034266 | 2.4542e-05 | 1 | 2
211 | 3.5167 | 4.9786 | 11.9658 | 5 | 12 | 71.0992 | 40 | 0.03418 | 3.3264 | -8.6755e-05 | 0.47549 | 4.5004 | 0 | 4.9759 |  | 15.3759 | 4 | 15.3759 | 71.0992 | 35.5496 | 15 | 35 | 0.54959 | -103.7166 | 0.03418 | 5.4222e-05 | 1 | 0
212 | 3.5333 | 4.9787 | 11.966 | 5 | 12 | 71.3755 | 40 | 0.034046 | 3.3604 | -0.0001335 | 0.47363 | 4.5464 | 0 | 5.0201 |  | 15.4201 | 4 | 15.4201 | 71.3755 | 35.6877 | 15 | 35 | 0.68773 | -103.0288 | 0.034046 | 8.344e-05 | 1 | 0
213 | 3.55 | 4.9788 | 11.9661 | 5 | 12 | 71.6462 | 40 | 0.033867 | 3.3943 | -0.00017946 | 0.47114 | 4.5923 | 0 | 5.0634 |  | 15.4634 | 4 | 15.4634 | 71.6462 | 35.8231 | 15 | 35 | 0.82312 | -102.2057 | 0.033867 | 0.00011216 | 1 | 0
214 | 3.5667 | 4.979 | 11.9664 | 5 | 12 | 71.9112 | 40 | 0.033642 | 3.4279 | -0.00022457 | 0.46801 | 4.6378 | 0 | 5.1058 |  | 15.5058 | 4 | 15.5058 | 71.9112 | 35.9556 | 15 | 35 | 0.95559 | -101.2501 | 0.033642 | 0.00014035 | 1 | 0
215 | 3.5833 | 4.9791 | 11.9666 | 5 | 12 | 72.17 | 40 | 0.033373 | 3.4613 | -0.00026877 | 0.46427 | 4.6829 | 0 | 5.1472 |  | 15.5472 | 4 | 15.5472 | 72.17 | 36.085 | 15 | 35 | 1.085 | -100.1651 | 0.033373 | 0.00016798 | 1 | 0
216 | 3.6 | 4.9793 | 11.9669 | 5 | 12 | 72.4224 | 40 | 0.033061 | 3.4944 | -0.00031203 | 0.45993 | 4.7277 | 0 | 5.1876 |  | 15.5876 | 4 | 15.5876 | 72.4224 | 36.2112 | 15 | 35 | 1.2112 | -98.9539 | 0.033061 | 0.00019502 | 1 | 0
217 | 3.6167 | 4.9796 | 11.9673 | 5 | 12 | 72.6682 | 40 | 0.032707 | 3.5271 | -0.00035429 | 0.455 | 4.7719 | 0 | 5.2269 |  | 15.6269 | 4 | 15.6269 | 72.6682 | 36.3341 | 15 | 35 | 1.3341 | -97.6198 | 0.032707 | 0.00022143 | 1 | 0
218 | 3.6333 | 4.9798 | 11.9677 | 5 | 12 | 72.907 | 40 | 0.032311 | 3.5594 | -0.0003955 | 0.4495 | 4.8156 | 0 | 5.2651 |  | 15.6651 | 4 | 15.6651 | 72.907 | 36.4535 | 15 | 35 | 1.4535 | -96.1662 | 0.032311 | 0.00024719 | 1 | 0
219 | 3.65 | 4.9801 | 11.9681 | 5 | 12 | 73.1387 | 40 | 0.031876 | 3.5913 | -0.00043563 | 0.44344 | 4.8588 | 0 | 5.3022 |  | 15.7022 | 4 | 15.7022 | 73.1387 | 36.5694 | 15 | 35 | 1.5694 | -94.5969 | 0.031876 | 0.00027227 | 1 | 0
220 | 3.6667 | 4.9804 | 11.9686 | 5 | 12 | 73.363 | 40 | 0.031401 | 3.6227 | -0.00047462 | 0.43684 | 4.9012 | 0 | 5.3381 |  | 15.7381 | 4 | 15.7381 | 73.363 | 36.6815 | 15 | 35 | 1.6815 | -92.9154 | 0.031401 | 0.00029664 | 1 | 0
221 | 3.6833 | 4.9807 | 11.9691 | 5 | 12 | 73.5796 | 40 | 0.030889 | 3.6535 | -0.00051244 | 0.42971 | 4.943 | 0 | 5.3727 |  | 15.7727 | 4 | 15.7727 | 73.5796 | 36.7898 | 15 | 35 | 1.7898 | -91.1256 | 0.030889 | 0.00032028 | 1 | 0
222 | 3.7 | 4.981 | 11.9697 | 5 | 12 | 73.7884 | 40 | 0.03034 | 3.6839 | -0.00054906 | 0.42207 | 4.9841 | 0 | 5.4061 |  | 15.8061 | 4 | 15.8061 | 73.7884 | 36.8942 | 15 | 35 | 1.8942 | -89.2314 | 0.03034 | 0.00034316 | 1 | 0
223 | 3.7167 | 4.9814 | 11.9702 | 5 | 12 | 73.9892 | 40 | 0.029755 | 3.7136 | -0.00058442 | 0.41394 | 5.0243 | 0 | 5.4383 |  | 15.8383 | 4 | 15.8383 | 73.9892 | 36.9946 | 15 | 35 | 1.9946 | -87.2368 | 0.029755 | 0.00036527 | 1 | 0
224 | 3.7333 | 4.9818 | 11.9709 | 5 | 12 | 74.1818 | 40 | 0.029137 | 3.7428 | -0.00061852 | 0.40534 | 5.0638 | 0 | 5.4691 |  | 15.8691 | 4 | 15.8691 | 74.1818 | 37.0909 | 15 | 35 | 2.0909 | -85.1459 | 0.029137 | 0.00038657 | 1 | 0
225 | 3.75 | 4.9822 | 11.9715 | 5 | 12 | 74.366 | 40 | 0.028485 | 3.7713 | -0.0006513 | 0.39628 | 5.1023 | 0 | 5.4986 |  | 15.8986 | 4 | 15.8986 | 74.366 | 37.183 | 15 | 35 | 2.183 | -82.9629 | 0.028485 | 0.00040706 | 1 | 0
226 | 3.7667 | 4.9826 | 11.9722 | 5 | 12 | 74.5418 | 40 | 0.027803 | 3.7991 | -0.00068274 | 0.38678 | 5.1399 | 0 | 5.5267 |  | 15.9267 | 4 | 15.9267 | 74.5418 | 37.2709 | 15 | 35 | 2.2709 | -80.692 | 0.027803 | 0.00042671 | 1 | 0
227 | 3.7833 | 4.9831 | 11.9729 | 5 | 12 | 74.7089 | 40 | 0.02709 | 3.8262 | -0.00071282 | 0.37686 | 5.1766 | 0 | 5.5534 |  | 15.9534 | 4 | 15.9534 | 74.7089 | 37.3544 | 15 | 35 | 2.3544 | -78.3376 | 0.02709 | 0.00044551 | 1 | 0
228 | 3.8 | 4.9835 | 11.9737 | 5 | 12 | 74.8672 | 40 | 0.026348 | 3.8525 | -0.00074152 | 0.36655 | 5.2122 | 0 | 5.5788 |  | 15.9788 | 4 | 15.9788 | 74.8672 | 37.4336 | 15 | 35 | 2.4336 | -75.904 | 0.026348 | 0.00046345 | 1 | 0
229 | 3.8167 | 4.984 | 11.9744 | 5 | 12 | 75.0167 | 40 | 0.02558 | 3.8781 | -0.0007688 | 0.35585 | 5.2468 | 0 | 5.6027 |  | 16.0027 | 4 | 16.0027 | 75.0167 | 37.5083 | 15 | 35 | 2.5083 | -73.3956 | 0.02558 | 0.0004805 | 1 | 0
230 | 3.8333 | 4.9845 | 11.9752 | 5 | 12 | 75.1571 | 40 | 0.024785 | 3.9029 | -0.00079464 | 0.3448 | 5.2803 | 0 | 5.6251 |  | 16.0251 | 4 | 16.0251 | 75.1571 | 37.5786 | 15 | 35 | 2.5786 | -70.8171 | 0.024785 | 0.00049665 | 1 | 0
231 | 3.85 | 4.985 | 11.976 | 5 | 12 | 75.2886 | 40 | 0.023966 | 3.9268 | -0.00081904 | 0.3334 | 5.3128 | 0 | 5.6462 |  | 16.0462 | 4 | 16.0462 | 75.2886 | 37.6443 | 15 | 35 | 2.6443 | -68.1728 | 0.023966 | 0.0005119 | 1 | 0
232 | 3.8667 | 4.9855 | 11.9769 | 5 | 12 | 75.4109 | 40 | 0.023124 | 3.95 | -0.00084198 | 0.32169 | 5.3441 | 0 | 5.6657 |  | 16.0657 | 4 | 16.0657 | 75.4109 | 37.7055 | 15 | 35 | 2.7055 | -65.4673 | 0.023124 | 0.00052624 | 1 | 0
233 | 3.8833 | 4.9861 | 11.9777 | 5 | 12 | 75.5241 | 40 | 0.02226 | 3.9722 | -0.00086344 | 0.30968 | 5.3742 | 0 | 5.6838 |  | 16.0838 | 4 | 16.0838 | 75.5241 | 37.762 | 15 | 35 | 2.762 | -62.7053 | 0.02226 | 0.00053965 | 1 | 0
234 | 3.9 | 4.9866 | 11.9786 | 5 | 12 | 75.628 | 40 | 0.021377 | 3.9936 | -0.00088341 | 0.29739 | 5.4031 | 0 | 5.7005 |  | 16.1005 | 4 | 16.1005 | 75.628 | 37.814 | 15 | 35 | 2.814 | -59.8913 | 0.021377 | 0.00055213 | 1 | 0
235 | 3.9167 | 4.9872 | 11.9795 | 5 | 12 | 75.7227 | 40 | 0.020475 | 4.0141 | -0.00090189 | 0.28484 | 5.4308 | 0 | 5.7156 |  | 16.1156 | 4 | 16.1156 | 75.7227 | 37.8614 | 15 | 35 | 2.8614 | -57.0299 | 0.020475 | 0.00056368 | 1 | 0
236 | 3.9333 | 4.9878 | 11.9804 | 5 | 12 | 75.8082 | 40 | 0.019556 | 4.0336 | -0.00091886 | 0.27206 | 5.4573 | 0 | 5.7293 |  | 16.1293 | 4 | 16.1293 | 75.8082 | 37.9041 | 15 | 35 | 2.9041 | -54.1258 | 0.019556 | 0.00057429 | 1 | 0
237 | 3.95 | 4.9884 | 11.9814 | 5 | 12 | 75.8844 | 40 | 0.018622 | 4.0522 | -0.00093432 | 0.25906 | 5.4824 | 0 | 5.7415 |  | 16.1415 | 4 | 16.1415 | 75.8844 | 37.9422 | 15 | 35 | 2.9422 | -51.1836 | 0.018622 | 0.00058395 | 1 | 0
238 | 3.9667 | 4.989 | 11.9823 | 5 | 12 | 75.9514 | 40 | 0.017674 | 4.0699 | -0.00094828 | 0.24587 | 5.5064 | 0 | 5.7522 |  | 16.1522 | 4 | 16.1522 | 75.9514 | 37.9757 | 15 | 35 | 2.9757 | -48.2079 | 0.017674 | 0.00059267 | 1 | 0
239 | 3.9833 | 4.9896 | 11.9833 | 5 | 12 | 76.0092 | 40 | 0.016713 | 4.0866 | -0.00096072 | 0.2325 | 5.529 | 0 | 5.7615 |  | 16.1615 | 4 | 16.1615 | 76.0092 | 38.0046 | 15 | 35 | 3.0046 | -45.2033 | 0.016713 | 0.00060045 | 1 | 0
240 | 4 | 4.9902 | 11.9843 | 5 | 12 | 76.0578 | 40 | 0.015741 | 4.1024 | -0.00097166 | 0.21899 | 5.5503 | 0 | 5.7693 |  | 16.1693 | 4 | 16.1693 | 76.0578 | 38.0289 | 15 | 35 | 3.0289 | -42.1744 | 0.015741 | 0.00060729 | 1 | 0
241 | 4.0167 | 4.9908 | 11.9852 | 5 | 12 | 76.0974 | 40 | 0.01476 | 4.1171 | -0.0009811 | 0.20534 | 5.5702 | 0 | 5.7756 |  | 16.1756 | 4 | 16.1756 | 76.0974 | 38.0487 | 15 | 35 | 3.0487 | -39.1257 | 0.01476 | 0.00061319 | 1 | 0
242 | 4.0333 | 4.9914 | 11.9862 | 5 | 12 | 76.1278 | 40 | 0.013771 | 4.1309 | -0.00098904 | 0.19158 | 5.5889 | 0 | 5.7804 |  | 16.1804 | 4 | 16.1804 | 76.1278 | 38.0639 | 15 | 35 | 3.0639 | -36.0618 | 0.013771 | 0.00061815 | 1 | 0
243 | 4.05 | 4.992 | 11.9872 | 5 | 12 | 76.1493 | 40 | 0.012776 | 4.1437 | -0.00099549 | 0.17773 | 5.6062 | 0 | 5.7839 |  | 16.1839 | 4 | 16.1839 | 76.1493 | 38.0746 | 15 | 35 | 3.0746 | -32.9871 | 0.012776 | 0.00062218 | 1 | 0
244 | 4.0667 | 4.9926 | 11.9882 | 5 | 12 | 76.1619 | 40 | 0.011775 | 4.1555 | -0.0010005 | 0.16381 | 5.6221 | 0 | 5.7859 |  | 16.1859 | 4 | 16.1859 | 76.1619 | 38.0809 | 15 | 35 | 3.0809 | -29.9062 | 0.011775 | 0.00062529 | 1 | 0
245 | 4.0833 | 4.9933 | 11.9892 | 5 | 12 | 76.1657 | 40 | 0.010771 | 4.1662 | -0.001004 | 0.14985 | 5.6367 | 0 | 5.7865 |  | 16.1865 | 4 | 16.1865 | 76.1657 | 38.0828 | 15 | 35 | 3.0828 | -26.8234 | 0.010771 | 0.00062748 | 1 | 0
246 | 4.1 | 4.9939 | 11.9902 | 5 | 12 | 76.1608 | 40 | 0.0097653 | 4.176 | -0.001006 | 0.13585 | 5.6499 | 0 | 5.7857 |  | 16.1857 | 4 | 16.1857 | 76.1608 | 38.0804 | 15 | 35 | 3.0804 | -23.743 | 0.0097653 | 0.00062876 | 1 | 0
247 | 4.1167 | 4.9945 | 11.9912 | 5 | 12 | 76.1473 | 40 | 0.0087587 | 4.1848 | -0.0010066 | 0.12185 | 5.6617 | 0 | 5.7836 |  | 16.1836 | 4 | 16.1836 | 76.1473 | 38.0736 | 15 | 35 | 3.0736 | -20.6693 | 0.0087587 | 0.00062915 | 1 | 0
248 | 4.1333 | 4.9952 | 11.9922 | 5 | 12 | 76.1254 | 40 | 0.0077528 | 4.1925 | -0.0010058 | 0.10785 | 5.6722 | 0 | 5.7801 |  | 16.1801 | 4 | 16.1801 | 76.1254 | 38.0627 | 15 | 35 | 3.0627 | -17.6066 | 0.0077528 | 0.00062865 | 1 | 0
249 | 4.15 | 4.9958 | 11.9933 | 5 | 12 | 76.0952 | 40 | 0.0067492 | 4.1993 | -0.0010036 | 0.093892 | 5.6813 | 0 | 5.7752 |  | 16.1752 | 4 | 16.1752 | 76.0952 | 38.0476 | 15 | 35 | 3.0476 | -14.559 | 0.0067492 | 0.00062728 | 1 | 0
250 | 4.1667 | 4.9964 | 11.9943 | 5 | 12 | 76.0569 | 40 | 0.0057491 | 4.205 | -0.0010001 | 0.079979 | 5.6891 | 0 | 5.7691 |  | 16.1691 | 4 | 16.1691 | 76.0569 | 38.0284 | 15 | 35 | 3.0284 | -11.5306 | 0.0057491 | 0.00062504 | 1 | 0
251 | 4.1833 | 4.997 | 11.9952 | 5 | 12 | 76.0105 | 40 | 0.004754 | 4.2098 | -0.00099514 | 0.066135 | 5.6956 | 0 | 5.7617 |  | 16.1617 | 4 | 16.1617 | 76.0105 | 38.0053 | 15 | 35 | 3.0053 | -8.5253 | 0.004754 | 0.00062196 | 1 | 0
252 | 4.2 | 4.9976 | 11.9962 | 5 | 12 | 75.9564 | 40 | 0.0037651 | 4.2135 | -0.00098888 | 0.052378 | 5.7006 | 0 | 5.753 |  | 16.153 | 4 | 16.153 | 75.9564 | 37.9782 | 15 | 35 | 2.9782 | -5.5471 | 0.0037651 | 0.00061805 | 1 | 0
253 | 4.2167 | 4.9983 | 11.9972 | 5 | 12 | 75.8946 | 40 | 0.0027838 | 4.2163 | -0.00098131 | 0.038727 | 5.7044 | 0 | 5.7431 |  | 16.1431 | 4 | 16.1431 | 75.8946 | 37.9473 | 15 | 35 | 2.9473 | -2.5998 | 0.0027838 | 0.00061332 | 1 | 0
254 | 4.2333 | 4.9989 | 11.9982 | 5 | 12 | 75.8254 | 40 | 0.0018113 | 4.2181 | -0.00097247 | 0.025198 | 5.7069 | 0 | 5.7321 |  | 16.1321 | 4 | 16.1321 | 75.8254 | 37.9127 | 15 | 35 | 2.9127 | 0.31285 | 0.0018113 | 0.0006078 | 1 | 0
255 | 4.25 | 4.9995 | 11.9992 | 5 | 12 | 75.7489 | 40 | 0.00084893 | 4.219 | -0.00096239 | 0.01181 | 5.708 | 0 | 5.7198 |  | 16.1198 | 4 | 16.1198 | 75.7489 | 37.8744 | 15 | 35 | 2.8744 | 3.1873 | 0.00084893 | 0.00060149 | 1 | 0
256 | 4.2667 | 5.0001 | 12.0001 | 5 | 12 | 75.6653 | 40 | -0.00010216 | 4.2189 | -0.00095108 | -0.0014211 | 5.7079 | 0 | 5.7065 |  | 16.1065 | 4 | 16.1065 | 75.6653 | 37.8327 | 15 | 35 | 2.8327 | 6.02 | 0.00010216 | 0.00059443 | 1 | 0
257 | 4.2833 | 5.0007 | 12.001 | 5 | 12 | 75.5749 | 40 | -0.0010407 | 4.2178 | -0.00093859 | -0.014478 | 5.7065 | 0 | 5.692 |  | 16.092 | 4 | 16.092 | 75.5749 | 37.7875 | 15 | 35 | 2.7875 | 8.8074 | 0.0010407 | 0.00058662 | 1 | 0
258 | 4.3 | 5.0012 | 12.002 | 5 | 12 | 75.4779 | 40 | -0.0019657 | 4.2159 | -0.00092495 | -0.027346 | 5.7038 | 0 | 5.6765 |  | 16.0765 | 4 | 16.0765 | 75.4779 | 37.7389 | 15 | 35 | 2.7389 | 11.5463 | 0.0019657 | 0.00057809 | 1 | 0
259 | 4.3167 | 5.0018 | 12.0029 | 5 | 12 | 75.3744 | 40 | -0.0028759 | 4.213 | -0.00091019 | -0.040008 | 5.6999 | 0 | 5.6599 |  | 16.0599 | 4 | 16.0599 | 75.3744 | 37.6872 | 15 | 35 | 2.6872 | 14.2335 | 0.0028759 | 0.00056887 | 1 | 0
260 | 4.3333 | 5.0024 | 12.0038 | 5 | 12 | 75.2648 | 40 | -0.0037702 | 4.2092 | -0.00089435 | -0.05245 | 5.6948 | 0 | 5.6424 |  | 16.0424 | 4 | 16.0424 | 75.2648 | 37.6324 | 15 | 35 | 2.6324 | 16.8659 | 0.0037702 | 0.00055897 | 1 | 0
261 | 4.35 | 5.0029 | 12.0046 | 5 | 12 | 75.1492 | 40 | -0.0046477 | 4.2046 | -0.00087745 | -0.064657 | 5.6885 | 0 | 5.6239 |  | 16.0239 | 4 | 16.0239 | 75.1492 | 37.5746 | 15 | 35 | 2.5746 | 19.4405 | 0.0046477 | 0.00054841 | 1 | 0
262 | 4.3667 | 5.0034 | 12.0055 | 5 | 12 | 75.0279 | 40 | -0.0055072 | 4.1991 | -0.00085955 | -0.076614 | 5.6811 | 0 | 5.6045 |  | 16.0045 | 4 | 16.0045 | 75.0279 | 37.5139 | 15 | 35 | 2.5139 | 21.9545 | 0.0055072 | 0.00053722 | 1 | 0
263 | 4.3833 | 5.004 | 12.0063 | 5 | 12 | 74.9011 | 40 | -0.0063479 | 4.1927 | -0.00084068 | -0.08831 | 5.6725 | 0 | 5.5842 |  | 15.9842 | 4 | 15.9842 | 74.9011 | 37.4506 | 15 | 35 | 2.4506 | 24.405 | 0.0063479 | 0.00052543 | 1 | 0
264 | 4.4 | 5.0045 | 12.0072 | 5 | 12 | 74.7691 | 40 | -0.0071688 | 4.1855 | -0.00082088 | -0.099729 | 5.6628 | 0 | 5.5631 |  | 15.9631 | 4 | 15.9631 | 74.7691 | 37.3846 | 15 | 35 | 2.3846 | 26.7896 | 0.0071688 | 0.00051305 | 1 | 0
265 | 4.4167 | 5.005 | 12.008 | 5 | 12 | 74.6322 | 40 | -0.007969 | 4.1776 | -0.00080018 | -0.11086 | 5.652 | 0 | 5.5411 |  | 15.9411 | 4 | 15.9411 | 74.6322 | 37.3161 | 15 | 35 | 2.3161 | 29.1056 | 0.007969 | 0.00050011 | 1 | 0
266 | 4.4333 | 5.0055 | 12.0087 | 5 | 12 | 74.4905 | 40 | -0.0087476 | 4.1688 | -0.00077863 | -0.12169 | 5.6402 | 0 | 5.5185 |  | 15.9185 | 4 | 15.9185 | 74.4905 | 37.2452 | 15 | 35 | 2.2452 | 31.3509 | 0.0087476 | 0.00048664 | 1 | 0
267 | 4.45 | 5.0059 | 12.0095 | 5 | 12 | 74.3444 | 40 | -0.0095039 | 4.1593 | -0.00075627 | -0.13221 | 5.6273 | 0 | 5.4951 |  | 15.8951 | 4 | 15.8951 | 74.3444 | 37.1722 | 15 | 35 | 2.1722 | 33.5231 | 0.0095039 | 0.00047267 | 1 | 0
268 | 4.4667 | 5.0064 | 12.0102 | 5 | 12 | 74.1941 | 40 | -0.010237 | 4.1491 | -0.00073314 | -0.14241 | 5.6135 | 0 | 5.471 |  | 15.871 | 4 | 15.871 | 74.1941 | 37.097 | 15 | 35 | 2.097 | 35.6201 | 0.010237 | 0.00045821 | 1 | 0
269 | 4.4833 | 5.0068 | 12.0109 | 5 | 12 | 74.0398 | 40 | -0.010946 | 4.1381 | -0.00070928 | -0.15228 | 5.5987 | 0 | 5.4464 |  | 15.8464 | 4 | 15.8464 | 74.0398 | 37.0199 | 15 | 35 | 2.0199 | 37.64 | 0.010946 | 0.0004433 | 1 | 0
270 | 4.5 | 5.0073 | 12.0116 | 5 | 12 | 73.8819 | 40 | -0.011631 | 4.1265 | -0.00068474 | -0.16181 | 5.5829 | 0 | 5.4211 |  | 15.8211 | 4 | 15.8211 | 73.8819 | 36.941 | 15 | 35 | 1.941 | 39.581 | 0.011631 | 0.00042796 | 1 | 0
271 | 4.5167 | 5.0077 | 12.0123 | 5 | 12 | 73.7207 | 40 | -0.012291 | 4.1142 | -0.00065956 | -0.17098 | 5.5663 | 0 | 5.3953 |  | 15.7953 | 4 | 15.7953 | 73.7207 | 36.8603 | 15 | 35 | 1.8603 | 41.4413 | 0.012291 | 0.00041223 | 1 | 0
272 | 4.5333 | 5.0081 | 12.0129 | 5 | 12 | 73.5563 | 40 | -0.012924 | 4.1013 | -0.00063379 | -0.1798 | 5.5488 | 0 | 5.369 |  | 15.769 | 4 | 15.769 | 73.5563 | 36.7781 | 15 | 35 | 1.7781 | 43.2194 | 0.012924 | 0.00039612 | 1 | 0
273 | 4.55 | 5.0085 | 12.0135 | 5 | 12 | 73.389 | 40 | -0.013532 | 4.0878 | -0.00060746 | -0.18825 | 5.5305 | 0 | 5.3422 |  | 15.7422 | 4 | 15.7422 | 73.389 | 36.6945 | 15 | 35 | 1.6945 | 44.9139 | 0.013532 | 0.00037966 | 1 | 0
274 | 4.5667 | 5.0088 | 12.0141 | 5 | 12 | 73.2192 | 40 | -0.014112 | 4.0736 | -0.00058062 | -0.19633 | 5.5114 | 0 | 5.3151 |  | 15.7151 | 4 | 15.7151 | 73.2192 | 36.6096 | 15 | 35 | 1.6096 | 46.5236 | 0.014112 | 0.00036288 | 1 | 0
275 | 4.5833 | 5.0092 | 12.0147 | 5 | 12 | 73.0471 | 40 | -0.014666 | 4.059 | -0.00055331 | -0.20402 | 5.4916 | 0 | 5.2875 |  | 15.6875 | 4 | 15.6875 | 73.0471 | 36.5235 | 15 | 35 | 1.5235 | 48.0471 | 0.014666 | 0.00034582 | 1 | 0
276 | 4.6 | 5.0095 | 12.0152 | 5 | 12 | 72.8729 | 40 | -0.015191 | 4.0438 | -0.00052559 | -0.21134 | 5.471 | 0 | 5.2597 |  | 15.6597 | 4 | 15.6597 | 72.8729 | 36.4365 | 15 | 35 | 1.4365 | 49.4836 | 0.015191 | 0.00032849 | 1 | 0
277 | 4.6167 | 5.0098 | 12.0157 | 5 | 12 | 72.697 | 40 | -0.015689 | 4.0281 | -0.00049748 | -0.21826 | 5.4498 | 0 | 5.2315 |  | 15.6315 | 4 | 15.6315 | 72.697 | 36.3485 | 15 | 35 | 1.3485 | 50.8321 | 0.015689 | 0.00031093 | 1 | 0
278 | 4.6333 | 5.0101 | 12.0162 | 5 | 12 | 72.5196 | 40 | -0.016158 | 4.0119 | -0.00046905 | -0.22478 | 5.4279 | 0 | 5.2031 |  | 15.6031 | 4 | 15.6031 | 72.5196 | 36.2598 | 15 | 35 | 1.2598 | 52.0919 | 0.016158 | 0.00029316 | 1 | 0
279 | 4.65 | 5.0104 | 12.0166 | 5 | 12 | 72.341 | 40 | -0.016598 | 3.9953 | -0.00044033 | -0.23091 | 5.4055 | 0 | 5.1746 |  | 15.5746 | 4 | 15.5746 | 72.341 | 36.1705 | 15 | 35 | 1.1705 | 53.2624 | 0.016598 | 0.00027521 | 1 | 0
280 | 4.6667 | 5.0106 | 12.017 | 5 | 12 | 72.1614 | 40 | -0.01701 | 3.9783 | -0.00041136 | -0.23663 | 5.3824 | 0 | 5.1458 |  | 15.5458 | 4 | 15.5458 | 72.1614 | 36.0807 | 15 | 35 | 1.0807 | 54.343 | 0.01701 | 0.0002571 | 1 | 0
281 | 4.6833 | 5.0109 | 12.0174 | 5 | 12 | 71.9811 | 40 | -0.017392 | 3.9609 | -0.0003822 | -0.24195 | 5.3589 | 0 | 5.117 |  | 15.517 | 4 | 15.517 | 71.9811 | 35.9905 | 15 | 35 | 0.99054 | 55.3336 | 0.017392 | 0.00023887 | 1 | 0
282 | 4.7 | 5.0111 | 12.0177 | 5 | 12 | 71.8003 | 40 | -0.017745 | 3.9432 | -0.00035288 | -0.24686 | 5.3349 | 0 | 5.0881 |  | 15.4881 | 4 | 15.4881 | 71.8003 | 35.9002 | 15 | 35 | 0.90017 | 56.2338 | 0.017745 | 0.00022055 | 1 | 0
283 | 4.7167 | 5.0113 | 12.0181 | 5 | 12 | 71.6194 | 40 | -0.018068 | 3.9251 | -0.00032344 | -0.25136 | 5.3105 | 0 | 5.0591 |  | 15.4591 | 4 | 15.4591 | 71.6194 | 35.8097 | 15 | 35 | 0.80972 | 57.0435 | 0.018068 | 0.00020215 | 1 | 0
284 | 4.7333 | 5.0115 | 12.0184 | 5 | 12 | 71.4386 | 40 | -0.018362 | 3.9068 | -0.00029393 | -0.25544 | 5.2856 | 0 | 5.0302 |  | 15.4302 | 4 | 15.4302 | 71.4386 | 35.7193 | 15 | 35 | 0.71931 | 57.7628 | 0.018362 | 0.00018371 | 1 | 0
285 | 4.75 | 5.0116 | 12.0186 | 5 | 12 | 71.2581 | 40 | -0.018626 | 3.8881 | -0.0002644 | -0.25912 | 5.2604 | 0 | 5.0013 |  | 15.4013 | 4 | 15.4013 | 71.2581 | 35.6291 | 15 | 35 | 0.62906 | 58.3919 | 0.018626 | 0.00016525 | 1 | 0
286 | 4.7667 | 5.0118 | 12.0189 | 5 | 12 | 71.0782 | 40 | -0.018861 | 3.8693 | -0.00023488 | -0.26239 | 5.2349 | 0 | 4.9725 |  | 15.3725 | 4 | 15.3725 | 71.0782 | 35.5391 | 15 | 35 | 0.53911 | 58.931 | 0.018861 | 0.0001468 | 1 | 0
287 | 4.7833 | 5.0119 | 12.0191 | 5 | 12 | 70.8991 | 40 | -0.019067 | 3.8502 | -0.00020541 | -0.26525 | 5.2091 | 0 | 4.9439 |  | 15.3439 | 4 | 15.3439 | 70.8991 | 35.4496 | 15 | 35 | 0.44957 | 59.3805 | 0.019067 | 0.00012838 | 1 | 0
288 | 4.8 | 5.012 | 12.0192 | 5 | 12 | 70.7211 | 40 | -0.019243 | 3.831 | -0.00017604 | -0.2677 | 5.1831 | 0 | 4.9154 |  | 15.3154 | 4 | 15.3154 | 70.7211 | 35.3606 | 15 | 35 | 0.36056 | 59.7411 | 0.019243 | 0.00011002 | 1 | 0
289 | 4.8167 | 5.0121 | 12.0194 | 5 | 12 | 70.5444 | 40 | -0.01939 | 3.8116 | -0.0001468 | -0.26974 | 5.1568 | 0 | 4.8871 |  | 15.2871 | 4 | 15.2871 | 70.5444 | 35.2722 | 15 | 35 | 0.2722 | 60.0133 | 0.01939 | 9.1748e-05 | 1 | 0
290 | 4.8333 | 5.0122 | 12.0195 | 5 | 12 | 70.3692 | 40 | -0.019507 | 3.7921 | -0.00011773 | -0.27138 | 5.1304 | 0 | 4.8591 |  | 15.2591 | 4 | 15.2591 | 70.3692 | 35.1846 | 15 | 35 | 0.1846 | 60.1979 | 0.019507 | 7.3583e-05 | 1 | 0
291 | 4.85 | 5.0122 | 12.0196 | 5 | 12 | 70.1958 | 40 | -0.019596 | 3.7725 | -8.888e-05 | -0.27261 | 5.1039 | 0 | 4.8313 |  | 15.2313 | 4 | 15.2313 | 70.1958 | 35.0979 | 15 | 35 | 0.097886 | 60.2958 | 0.019596 | 5.555e-05 | 1 | 0
292 | 4.8667 | 5.0123 | 12.0197 | 5 | 12 | 70.0243 | 40 | -0.019656 | 3.7528 | -6.0278e-05 | -0.27345 | 5.0773 | 0 | 4.8039 |  | 15.2039 | 4 | 15.2039 | 70.0243 | 35.0122 | 15 | 35 | 0.01216 | 60.3079 | 0.019656 | 3.7674e-05 | 1 | 0
293 | 4.8833 | 5.0123 | 12.0197 | 5 | 12 | 69.8551 | 40 | -0.019688 | 3.7331 | -3.1963e-05 | -0.2739 | 5.0507 | 0 | 4.7768 |  | 15.1768 | 4 | 15.1768 | 69.8551 | 34.9275 | 15 | 35 | -0.072471 | 60.2355 | 0.019688 | 1.9977e-05 | 1 | 0
294 | 4.9 | 5.0123 | 12.0197 | 5 | 12 | 69.6882 | 40 | -0.019692 | 3.7134 | -3.9705e-06 | -0.27395 | 5.0241 | 0 | 4.7501 |  | 15.1501 | 4 | 15.1501 | 69.6882 | 34.8441 | 15 | 35 | -0.1559 | 60.0796 | 0.019692 | 2.4816e-06 | 1 | 0
295 | 4.9167 | 5.0123 | 12.0197 | 5 | 12 | 69.5239 | 40 | -0.019669 | 3.6938 | 2.3664e-05 | -0.27362 | 4.9975 | 0 | 4.7238 |  | 15.1238 | 4 | 15.1238 | 69.5239 | 34.762 | 15 | 35 | -0.23803 | 59.8415 | 0.019669 | -1.479e-05 | -1 | -2
296 | 4.9333 | 5.0123 | 12.0196 | 5 | 12 | 69.3625 | 40 | -0.019618 | 3.6742 | 5.0907e-05 | -0.27291 | 4.9709 | 0 | 4.698 |  | 15.098 | 4 | 15.098 | 69.3625 | 34.6812 | 15 | 35 | -0.31876 | 59.5228 | 0.019618 | -3.1817e-05 | -1 | 0
297 | 4.95 | 5.0122 | 12.0195 | 5 | 12 | 69.204 | 40 | -0.01954 | 3.6546 | 7.7725e-05 | -0.27183 | 4.9445 | 0 | 4.6726 |  | 15.0726 | 4 | 15.0726 | 69.204 | 34.602 | 15 | 35 | -0.398 | 59.1248 | 0.01954 | -4.8578e-05 | -1 | 0
298 | 4.9667 | 5.0121 | 12.0194 | 5 | 12 | 69.0487 | 40 | -0.019436 | 3.6352 | 0.00010409 | -0.27039 | 4.9182 | 0 | 4.6478 |  | 15.0478 | 4 | 15.0478 | 69.0487 | 34.5244 | 15 | 35 | -0.47565 | 58.6491 | 0.019436 | -6.5053e-05 | -1 | 0
299 | 4.9833 | 5.0121 | 12.0193 | 5 | 12 | 68.8968 | 40 | -0.019306 | 3.6159 | 0.00012996 | -0.26858 | 4.8921 | 0 | 4.6235 |  | 15.0235 | 4 | 15.0235 | 68.8968 | 34.4484 | 15 | 35 | -0.55162 | 58.0975 | 0.019306 | -8.1224e-05 | -1 | 0
300 | 5 | 5.012 | 12.0192 | 5 | 12 | 68.7483 | 40 | -0.019151 | 3.5967 | 0.00015531 | -0.26642 | 4.8661 | 0 | 4.5997 |  | 14.9997 | 4 | 14.9997 | 68.7483 | 34.3742 | 15 | 35 | -0.62584 | 57.4717 | 0.019151 | -9.7071e-05 | -1 | 0
301 | 5.0167 | 5.0119 | 12.019 | 5 | 12 | 68.6036 | 40 | -0.018971 | 3.5777 | 0.00018012 | -0.26391 | 4.8405 | 0 | 4.5766 |  | 14.9766 | 4 | 14.9766 | 68.6036 | 34.3018 | 15 | 35 | -0.69821 | 56.7734 | 0.018971 | -0.00011258 | -1 | 0
302 | 5.0333 | 5.0117 | 12.0188 | 5 | 12 | 68.4627 | 40 | -0.018766 | 3.559 | 0.00020436 | -0.26107 | 4.8151 | 0 | 4.554 |  | 14.954 | 4 | 14.954 | 68.4627 | 34.2313 | 15 | 35 | -0.76867 | 56.0048 | 0.018766 | -0.00012772 | -1 | 0
303 | 5.05 | 5.0116 | 12.0185 | 5 | 12 | 68.3257 | 40 | -0.018538 | 3.5404 | 0.00022799 | -0.2579 | 4.79 | 0 | 4.5321 |  | 14.9321 | 4 | 14.9321 | 68.3257 | 34.1629 | 15 | 35 | -0.83714 | 55.1676 | 0.018538 | -0.00014249 | -1 | 0
304 | 5.0667 | 5.0114 | 12.0183 | 5 | 12 | 68.1929 | 40 | -0.018287 | 3.5222 | 0.00025099 | -0.2544 | 4.7653 | 0 | 4.5109 |  | 14.9109 | 4 | 14.9109 | 68.1929 | 34.0965 | 15 | 35 | -0.90355 | 54.2641 | 0.018287 | -0.00015687 | -1 | 0
305 | 5.0833 | 5.0113 | 12.018 | 5 | 12 | 68.0644 | 40 | -0.018014 | 3.5041 | 0.00027335 | -0.2506 | 4.7409 | 0 | 4.4903 |  | 14.8903 | 4 | 14.8903 | 68.0644 | 34.0322 | 15 | 35 | -0.96782 | 53.2963 | 0.018014 | -0.00017084 | -1 | 0
306 | 5.1 | 5.0111 | 12.0177 | 5 | 12 | 67.9402 | 40 | -0.017719 | 3.4864 | 0.00029504 | -0.2465 | 4.7169 | 0 | 4.4704 |  | 14.8704 | 4 | 14.8704 | 67.9402 | 33.9701 | 15 | 35 | -1.0299 | 52.2664 | 0.017719 | -0.0001844 | -1 | 0
307 | 5.1167 | 5.0109 | 12.0174 | 5 | 12 | 67.8205 | 40 | -0.017403 | 3.469 | 0.00031602 | -0.2421 | 4.6934 | 0 | 4.4513 |  | 14.8513 | 4 | 14.8513 | 67.8205 | 33.9102 | 15 | 35 | -1.0898 | 51.1766 | 0.017403 | -0.00019751 | -1 | 0
308 | 5.1333 | 5.0107 | 12.0171 | 5 | 12 | 67.7054 | 40 | -0.017067 | 3.452 | 0.0003363 | -0.23742 | 4.6703 | 0 | 4.4329 |  | 14.8329 | 4 | 14.8329 | 67.7054 | 33.8527 | 15 | 35 | -1.1473 | 50.0293 | 0.017067 | -0.00021019 | -1 | 0
309 | 5.15 | 5.0104 | 12.0167 | 5 | 12 | 67.5951 | 40 | -0.016711 | 3.4352 | 0.00035584 | -0.23247 | 4.6477 | 0 | 4.4152 |  | 14.8152 | 4 | 14.8152 | 67.5951 | 33.7975 | 15 | 35 | -1.2025 | 48.8268 | 0.016711 | -0.0002224 | -1 | 0
310 | 5.1667 | 5.0102 | 12.0163 | 5 | 12 | 67.4895 | 40 | -0.016336 | 3.4189 | 0.00037462 | -0.22726 | 4.6256 | 0 | 4.3983 |  | 14.7983 | 4 | 14.7983 | 67.4895 | 33.7447 | 15 | 35 | -1.2553 | 47.5716 | 0.016336 | -0.00023414 | -1 | 0
311 | 5.1833 | 5.01 | 12.0159 | 5 | 12 | 67.3888 | 40 | -0.015943 | 3.403 | 0.00039264 | -0.2218 | 4.604 | 0 | 4.3822 |  | 14.7822 | 4 | 14.7822 | 67.3888 | 33.6944 | 15 | 35 | -1.3056 | 46.266 | 0.015943 | -0.0002454 | -1 | 0
312 | 5.2 | 5.0097 | 12.0155 | 5 | 12 | 67.2931 | 40 | -0.015534 | 3.3874 | 0.00040988 | -0.2161 | 4.583 | 0 | 4.3669 |  | 14.7669 | 4 | 14.7669 | 67.2931 | 33.6466 | 15 | 35 | -1.3534 | 44.9126 | 0.015534 | -0.00025617 | -1 | 0
313 | 5.2167 | 5.0094 | 12.0151 | 5 | 12 | 67.2024 | 40 | -0.015107 | 3.3723 | 0.00042632 | -0.21017 | 4.5626 | 0 | 4.3524 |  | 14.7524 | 4 | 14.7524 | 67.2024 | 33.6012 | 15 | 35 | -1.3988 | 43.5138 | 0.015107 | -0.00026645 | -1 | 0
314 | 5.2333 | 5.0092 | 12.0147 | 5 | 12 | 67.1168 | 40 | -0.014665 | 3.3577 | 0.00044194 | -0.20402 | 4.5427 | 0 | 4.3387 |  | 14.7387 | 4 | 14.7387 | 67.1168 | 33.5584 | 15 | 35 | -1.4416 | 42.0722 | 0.014665 | -0.00027621 | -1 | 0
315 | 5.25 | 5.0089 | 12.0142 | 5 | 12 | 67.0364 | 40 | -0.014209 | 3.3434 | 0.00045675 | -0.19766 | 4.5235 | 0 | 4.3258 |  | 14.7258 | 4 | 14.7258 | 67.0364 | 33.5182 | 15 | 35 | -1.4818 | 40.5904 | 0.014209 | -0.00028547 | -1 | 0
316 | 5.2667 | 5.0086 | 12.0137 | 5 | 12 | 66.9612 | 40 | -0.013738 | 3.3297 | 0.00047072 | -0.19112 | 4.5049 | 0 | 4.3138 |  | 14.7138 | 4 | 14.7138 | 66.9612 | 33.4806 | 15 | 35 | -1.5194 | 39.071 | 0.013738 | -0.0002942 | -1 | 0
317 | 5.2833 | 5.0083 | 12.0133 | 5 | 12 | 66.8912 | 40 | -0.013254 | 3.3165 | 0.00048385 | -0.18438 | 4.487 | 0 | 4.3026 |  | 14.7026 | 4 | 14.7026 | 66.8912 | 33.4456 | 15 | 35 | -1.5544 | 37.5166 | 0.013254 | -0.00030241 | -1 | 0
318 | 5.3 | 5.008 | 12.0128 | 5 | 12 | 66.8264 | 40 | -0.012758 | 3.3037 | 0.00049613 | -0.17748 | 4.4697 | 0 | 4.2922 |  | 14.6922 | 4 | 14.6922 | 66.8264 | 33.4132 | 15 | 35 | -1.5868 | 35.9298 | 0.012758 | -0.00031008 | -1 | 0
319 | 5.3167 | 5.0077 | 12.0123 | 5 | 12 | 66.767 | 40 | -0.01225 | 3.2914 | 0.00050756 | -0.17042 | 4.4531 | 0 | 4.2827 |  | 14.6827 | 4 | 14.6827 | 66.767 | 33.3835 | 15 | 35 | -1.6165 | 34.3133 | 0.01225 | -0.00031723 | -1 | 0
320 | 5.3333 | 5.0073 | 12.0117 | 5 | 12 | 66.7128 | 40 | -0.011732 | 3.2797 | 0.00051813 | -0.16321 | 4.4373 | 0 | 4.2741 |  | 14.6741 | 4 | 14.6741 | 66.7128 | 33.3564 | 15 | 35 | -1.6436 | 32.6697 | 0.011732 | -0.00032383 | -1 | 0
321 | 5.35 | 5.007 | 12.0112 | 5 | 12 | 66.664 | 40 | -0.011204 | 3.2685 | 0.00052784 | -0.15587 | 4.4221 | 0 | 4.2662 |  | 14.6662 | 4 | 14.6662 | 66.664 | 33.332 | 15 | 35 | -1.668 | 31.0017 | 0.011204 | -0.0003299 | -1 | 0
322 | 5.3667 | 5.0067 | 12.0107 | 5 | 12 | 66.6204 | 40 | -0.010668 | 3.2578 | 0.00053668 | -0.1484 | 4.4077 | 0 | 4.2593 |  | 14.6593 | 4 | 14.6593 | 66.6204 | 33.3102 | 15 | 35 | -1.6898 | 29.3119 | 0.010668 | -0.00033543 | -1 | 0
323 | 5.3833 | 5.0063 | 12.0101 | 5 | 12 | 66.5822 | 40 | -0.010123 | 3.2477 | 0.00054466 | -0.14083 | 4.394 | 0 | 4.2531 |  | 14.6531 | 4 | 14.6531 | 66.5822 | 33.2911 | 15 | 35 | -1.7089 | 27.603 | 0.010123 | -0.00034041 | -1 | 0
324 | 5.4 | 5.006 | 12.0096 | 5 | 12 | 66.5492 | 40 | -0.0095712 | 3.2382 | 0.00055177 | -0.13315 | 4.381 | 0 | 4.2479 |  | 14.6479 | 4 | 14.6479 | 66.5492 | 33.2746 | 15 | 35 | -1.7254 | 25.8776 | 0.0095712 | -0.00034485 | -1 | 0
325 | 5.4167 | 5.0056 | 12.009 | 5 | 12 | 66.5215 | 40 | -0.0090132 | 3.2291 | 0.00055801 | -0.12539 | 4.3688 | 0 | 4.2434 |  | 14.6434 | 4 | 14.6434 | 66.5215 | 33.2608 | 15 | 35 | -1.7392 | 24.1384 | 0.0090132 | -0.00034876 | -1 | 0
326 | 5.4333 | 5.0053 | 12.0084 | 5 | 12 | 66.4991 | 40 | -0.0084498 | 3.2207 | 0.00056339 | -0.11755 | 4.3574 | 0 | 4.2399 |  | 14.6399 | 4 | 14.6399 | 66.4991 | 33.2495 | 15 | 35 | -1.7505 | 22.3879 | 0.0084498 | -0.00035212 | -1 | 0
327 | 5.45 | 5.0049 | 12.0079 | 5 | 12 | 66.4818 | 40 | -0.0078819 | 3.2128 | 0.00056791 | -0.10965 | 4.3467 | 0 | 4.2371 |  | 14.6371 | 4 | 14.6371 | 66.4818 | 33.2409 | 15 | 35 | -1.7591 | 20.6288 | 0.0078819 | -0.00035495 | -1 | 0
328 | 5.4667 | 5.0046 | 12.0073 | 5 | 12 | 66.4697 | 40 | -0.0073103 | 3.2055 | 0.00057158 | -0.1017 | 4.3368 | 0 | 4.2351 |  | 14.6351 | 4 | 14.6351 | 66.4697 | 33.2348 | 15 | 35 | -1.7652 | 18.8636 | 0.0073103 | -0.00035724 | -1 | 0
329 | 5.4833 | 5.0042 | 12.0067 | 5 | 12 | 66.4627 | 40 | -0.0067359 | 3.1988 | 0.0005744 | -0.093707 | 4.3277 | 0 | 4.234 |  | 14.634 | 4 | 14.634 | 66.4627 | 33.2313 | 15 | 35 | -1.7687 | 17.095 | 0.0067359 | -0.000359 | -1 | 0
330 | 5.5 | 5.0038 | 12.0062 | 5 | 12 | 66.4607 | 40 | -0.0061595 | 3.1926 | 0.00057638 | -0.085689 | 4.3194 | 0 | 4.2337 |  | 14.6337 | 4 | 14.6337 | 66.4607 | 33.2303 | 15 | 35 | -1.7697 | 15.3253 | 0.0061595 | -0.00036024 | -1 | 0
331 | 5.5167 | 5.0035 | 12.0056 | 5 | 12 | 66.4637 | 40 | -0.005582 | 3.187 | 0.00057752 | -0.077655 | 4.3118 | 0 | 4.2342 |  | 14.6342 | 4 | 14.6342 | 66.4637 | 33.2319 | 15 | 35 | -1.7681 | 13.5571 | 0.005582 | -0.00036095 | -1 | 0
332 | 5.5333 | 5.0031 | 12.005 | 5 | 12 | 66.4716 | 40 | -0.0050042 | 3.182 | 0.00057785 | -0.069616 | 4.3051 | 0 | 4.2355 |  | 14.6355 | 4 | 14.6355 | 66.4716 | 33.2358 | 15 | 35 | -1.7642 | 11.793 | 0.0050042 | -0.00036115 | -1 | 0
333 | 5.55 | 5.0028 | 12.0044 | 5 | 12 | 66.4844 | 40 | -0.0044268 | 3.1776 | 0.00057735 | -0.061584 | 4.2991 | 0 | 4.2375 |  | 14.6375 | 4 | 14.6375 | 66.4844 | 33.2422 | 15 | 35 | -1.7578 | 10.0352 | 0.0044268 | -0.00036085 | -1 | 0
334 | 5.5667 | 5.0024 | 12.0039 | 5 | 12 | 66.5019 | 40 | -0.0038508 | 3.1737 | 0.00057606 | -0.05357 | 4.2939 | 0 | 4.2403 |  | 14.6403 | 4 | 14.6403 | 66.5019 | 33.251 | 15 | 35 | -1.749 | 8.2861 | 0.0038508 | -0.00036004 | -1 | 0
335 | 5.5833 | 5.002 | 12.0033 | 5 | 12 | 66.5241 | 40 | -0.0032768 | 3.1705 | 0.00057398 | -0.045585 | 4.2894 | 0 | 4.2439 |  | 14.6439 | 4 | 14.6439 | 66.5241 | 33.2621 | 15 | 35 | -1.7379 | 6.5482 | 0.0032768 | -0.00035873 | -1 | 0
336 | 5.6 | 5.0017 | 12.0027 | 5 | 12 | 66.5509 | 40 | -0.0027057 | 3.1678 | 0.00057111 | -0.03764 | 4.2858 | 0 | 4.2481 |  | 14.6481 | 4 | 14.6481 | 66.5509 | 33.2754 | 15 | 35 | -1.7246 | 4.8236 | 0.0027057 | -0.00035695 | -1 | 0
337 | 5.6167 | 5.0013 | 12.0021 | 5 | 12 | 66.5822 | 40 | -0.0021382 | 3.1656 | 0.00056749 | -0.029745 | 4.2829 | 0 | 4.2531 |  | 14.6531 | 4 | 14.6531 | 66.5822 | 33.2911 | 15 | 35 | -1.7089 | 3.1147 | 0.0021382 | -0.00035468 | -1 | 0
338 | 5.6333 | 5.001 | 12.0016 | 5 | 12 | 66.6178 | 40 | -0.0015751 | 3.164 | 0.00056312 | -0.021912 | 4.2808 | 0 | 4.2588 |  | 14.6588 | 4 | 14.6588 | 66.6178 | 33.3089 | 15 | 35 | -1.6911 | 1.4236 | 0.0015751 | -0.00035195 | -1 | 0
339 | 5.65 | 5.0006 | 12.001 | 5 | 12 | 66.6577 | 40 | -0.001017 | 3.163 | 0.00055801 | -0.014149 | 4.2794 | 0 | 4.2652 |  | 14.6652 | 4 | 14.6652 | 66.6577 | 33.3289 | 15 | 35 | -1.6711 | -0.24752 | 0.001017 | -0.00034876 | -1 | 0
340 | 5.6667 | 5.0003 | 12.0005 | 5 | 12 | 66.7018 | 40 | -0.00046485 | 3.1626 | 0.0005522 | -0.0064668 | 4.2788 | 0 | 4.2723 |  | 14.6723 | 4 | 14.6723 | 66.7018 | 33.3509 | 15 | 35 | -1.6491 | -1.8966 | 0.00046485 | -0.00034512 | -1 | 0
341 | 5.6833 | 4.9999 | 11.9999 | 5 | 12 | 66.7499 | 40 | 8.0824e-05 | 3.1626 | 0.00054568 | 0.0011244 | 4.2789 | 0 | 4.28 |  | 14.68 | 4 | 14.68 | 66.7499 | 33.375 | 15 | 35 | -1.625 | -3.5217 | 8.0824e-05 | -0.00034105 | -1 | 0
342 | 5.7 | 4.9996 | 11.9994 | 5 | 12 | 66.802 | 40 | 0.00061931 | 3.1633 | 0.00053848 | 0.0086155 | 4.2797 | 0 | 4.2883 |  | 14.6883 | 4 | 14.6883 | 66.802 | 33.401 | 15 | 35 | -1.599 | -5.1207 | 0.00061931 | -0.00033655 | -1 | 0
343 | 5.7167 | 4.9993 | 11.9989 | 5 | 12 | 66.8578 | 40 | 0.0011499 | 3.1644 | 0.00053062 | 0.015997 | 4.2813 | 0 | 4.2973 |  | 14.6973 | 4 | 14.6973 | 66.8578 | 33.4289 | 15 | 35 | -1.5711 | -6.6917 | 0.0011499 | -0.00033164 | -1 | 0
344 | 5.7333 | 4.999 | 11.9983 | 5 | 12 | 66.9174 | 40 | 0.0016721 | 3.1661 | 0.00052212 | 0.023261 | 4.2835 | 0 | 4.3068 |  | 14.7068 | 4 | 14.7068 | 66.9174 | 33.4587 | 15 | 35 | -1.5413 | -8.233 | 0.0016721 | -0.00032633 | -1 | 0
345 | 5.75 | 4.9986 | 11.9978 | 5 | 12 | 66.9805 | 40 | 0.0021851 | 3.1683 | 0.000513 | 0.030398 | 4.2865 | 0 | 4.3169 |  | 14.7169 | 4 | 14.7169 | 66.9805 | 33.4902 | 15 | 35 | -1.5098 | -9.7428 | 0.0021851 | -0.00032063 | -1 | 0
346 | 5.7667 | 4.9983 | 11.9973 | 5 | 12 | 67.047 | 40 | 0.0026883 | 3.171 | 0.00050328 | 0.037399 | 4.2901 | 0 | 4.3275 |  | 14.7275 | 4 | 14.7275 | 67.047 | 33.5235 | 15 | 35 | -1.4765 | -11.2193 | 0.0026883 | -0.00031455 | -1 | 0
347 | 5.7833 | 4.998 | 11.9968 | 5 | 12 | 67.1167 | 40 | 0.0031813 | 3.1741 | 0.00049299 | 0.044257 | 4.2944 | 0 | 4.3387 |  | 14.7387 | 4 | 14.7387 | 67.1167 | 33.5584 | 15 | 35 | -1.4416 | -12.661 | 0.0031813 | -0.00030812 | -1 | 0
348 | 5.8 | 4.9977 | 11.9963 | 5 | 12 | 67.1896 | 40 | 0.0036635 | 3.1778 | 0.00048213 | 0.050964 | 4.2994 | 0 | 4.3503 |  | 14.7503 | 4 | 14.7503 | 67.1896 | 33.5948 | 15 | 35 | -1.4052 | -14.0662 | 0.0036635 | -0.00030133 | -1 | 0
349 | 5.8167 | 4.9974 | 11.9959 | 5 | 12 | 67.2655 | 40 | 0.0041342 | 3.1819 | 0.00047074 | 0.057513 | 4.305 | 0 | 4.3625 |  | 14.7625 | 4 | 14.7625 | 67.2655 | 33.6328 | 15 | 35 | -1.3672 | -15.4334 | 0.0041342 | -0.00029421 | -1 | 0
350 | 5.8333 | 4.9971 | 11.9954 | 5 | 12 | 67.3442 | 40 | 0.004593 | 3.1865 | 0.00045884 | 0.063896 | 4.3112 | 0 | 4.3751 |  | 14.7751 | 4 | 14.7751 | 67.3442 | 33.6721 | 15 | 35 | -1.3279 | -16.7613 | 0.004593 | -0.00028677 | -1 | 0
351 | 5.85 | 4.9969 | 11.995 | 5 | 12 | 67.4257 | 40 | 0.0050395 | 3.1916 | 0.00044645 | 0.070107 | 4.318 | 0 | 4.3881 |  | 14.7881 | 4 | 14.7881 | 67.4257 | 33.7128 | 15 | 35 | -1.2872 | -18.0485 | 0.0050395 | -0.00027903 | -1 | 0
352 | 5.8667 | 4.9966 | 11.9945 | 5 | 12 | 67.5096 | 40 | 0.0054731 | 3.197 | 0.00043359 | 0.076139 | 4.3254 | 0 | 4.4015 |  | 14.8015 | 4 | 14.8015 | 67.5096 | 33.7548 | 15 | 35 | -1.2452 | -19.2936 | 0.0054731 | -0.000271 | -1 | 0
353 | 5.8833 | 4.9963 | 11.9941 | 5 | 12 | 67.596 | 40 | 0.0058934 | 3.2029 | 0.0004203 | 0.081986 | 4.3334 | 0 | 4.4154 |  | 14.8154 | 4 | 14.8154 | 67.596 | 33.798 | 15 | 35 | -1.202 | -20.4956 | 0.0058934 | -0.00026269 | -1 | 0
354 | 5.9 | 4.9961 | 11.9937 | 5 | 12 | 67.6846 | 40 | 0.0063 | 3.2092 | 0.00040659 | 0.087642 | 4.3419 | 0 | 4.4295 |  | 14.8295 | 4 | 14.8295 | 67.6846 | 33.8423 | 15 | 35 | -1.1577 | -21.6533 | 0.0063 | -0.00025412 | -1 | 0
355 | 5.9167 | 4.9958 | 11.9933 | 5 | 12 | 67.7754 | 40 | 0.0066924 | 3.2159 | 0.00039249 | 0.093102 | 4.351 | 0 | 4.4441 |  | 14.8441 | 4 | 14.8441 | 67.7754 | 33.8877 | 15 | 35 | -1.1123 | -22.7656 | 0.0066924 | -0.0002453 | -1 | 0
356 | 5.9333 | 4.9956 | 11.9929 | 5 | 12 | 67.868 | 40 | 0.0070705 | 3.223 | 0.00037802 | 0.098361 | 4.3605 | 0 | 4.4589 |  | 14.8589 | 4 | 14.8589 | 67.868 | 33.934 | 15 | 35 | -1.066 | -23.8316 | 0.0070705 | -0.00023626 | -1 | 0
357 | 5.95 | 4.9954 | 11.9926 | 5 | 12 | 67.9625 | 40 | 0.0074337 | 3.2304 | 0.00036321 | 0.10341 | 4.3706 | 0 | 4.474 |  | 14.874 | 4 | 14.874 | 67.9625 | 33.9812 | 15 | 35 | -1.0188 | -24.8504 | 0.0074337 | -0.000227 | -1 | 0
358 | 5.9667 | 4.9951 | 11.9922 | 5 | 12 | 68.0585 | 40 | 0.0077818 | 3.2382 | 0.00034808 | 0.10826 | 4.3811 | 0 | 4.4894 |  | 14.8894 | 4 | 14.8894 | 68.0585 | 34.0293 | 15 | 35 | -0.97074 | -25.8211 | 0.0077818 | -0.00021755 | -1 | 0
359 | 5.9833 | 4.9949 | 11.9919 | 5 | 12 | 68.1561 | 40 | 0.0081144 | 3.2463 | 0.00033266 | 0.11288 | 4.3921 | 0 | 4.505 |  | 14.905 | 4 | 14.905 | 68.1561 | 34.078 | 15 | 35 | -0.92197 | -26.7431 | 0.0081144 | -0.00020791 | -1 | 0
360 | 6 | 4.9947 | 11.9916 | 5 | 12 | 68.2549 | 40 | 0.0084314 | 3.2548 | 0.00031698 | 0.11729 | 4.4035 | 0 | 4.5208 |  | 14.9208 | 4 | 14.9208 | 68.2549 | 34.1275 | 15 | 35 | -0.87254 | -27.6156 | 0.0084314 | -0.00019811 | -1 | 0
361 | 6.0167 | 4.9945 | 11.9913 | 5 | 12 | 68.3549 | 40 | 0.0087324 | 3.2635 | 0.00030105 | 0.12148 | 4.4153 | 0 | 4.5368 |  | 14.9368 | 4 | 14.9368 | 68.3549 | 34.1775 | 15 | 35 | -0.82253 | -28.4382 | 0.0087324 | -0.00018816 | -1 | 0
362 | 6.0333 | 4.9944 | 11.991 | 5 | 12 | 68.456 | 40 | 0.0090173 | 3.2725 | 0.00028491 | 0.12545 | 4.4275 | 0 | 4.553 |  | 14.953 | 4 | 14.953 | 68.456 | 34.228 | 15 | 35 | -0.77202 | -29.2102 | 0.0090173 | -0.00017807 | -1 | 0
363 | 6.05 | 4.9942 | 11.9907 | 5 | 12 | 68.5578 | 40 | 0.0092859 | 3.2818 | 0.00026858 | 0.12918 | 4.4401 | 0 | 4.5693 |  | 14.9693 | 4 | 14.9693 | 68.5578 | 34.2789 | 15 | 35 | -0.72109 | -29.9313 | 0.0092859 | -0.00016786 | -1 | 0
364 | 6.0667 | 4.994 | 11.9905 | 5 | 12 | 68.6604 | 40 | 0.009538 | 3.2913 | 0.00025209 | 0.13269 | 4.453 | 0 | 4.5857 |  | 14.9857 | 4 | 14.9857 | 68.6604 | 34.3302 | 15 | 35 | -0.6698 | -30.6011 | 0.009538 | -0.00015756 | -1 | 0
365 | 6.0833 | 4.9939 | 11.9902 | 5 | 12 | 68.7635 | 40 | 0.0097735 | 3.3011 | 0.00023546 | 0.13596 | 4.4662 | 0 | 4.6022 |  | 15.0022 | 4 | 15.0022 | 68.7635 | 34.3818 | 15 | 35 | -0.61824 | -31.2193 | 0.0097735 | -0.00014716 | -1 | 0
366 | 6.1 | 4.9938 | 11.99 | 5 | 12 | 68.867 | 40 | 0.0099922 | 3.3111 | 0.00021871 | 0.13901 | 4.4797 | 0 | 4.6187 |  | 15.0187 | 4 | 15.0187 | 68.867 | 34.4335 | 15 | 35 | -0.56649 | -31.7858 | 0.0099922 | -0.00013669 | -1 | 0
367 | 6.1167 | 4.9936 | 11.9898 | 5 | 12 | 68.9708 | 40 | 0.010194 | 3.3213 | 0.00020188 | 0.14182 | 4.4935 | 0 | 4.6353 |  | 15.0353 | 4 | 15.0353 | 68.9708 | 34.4854 | 15 | 35 | -0.51461 | -32.3004 | 0.010194 | -0.00012617 | -1 | 0
368 | 6.1333 | 4.9935 | 11.9896 | 5 | 12 | 69.0746 | 40 | 0.010379 | 3.3317 | 0.00018498 | 0.14439 | 4.5076 | 0 | 4.6519 |  | 15.0519 | 4 | 15.0519 | 69.0746 | 34.5373 | 15 | 35 | -0.46269 | -32.7631 | 0.010379 | -0.00011561 | -1 | 0
369 | 6.15 | 4.9934 | 11.9895 | 5 | 12 | 69.1784 | 40 | 0.010547 | 3.3422 | 0.00016804 | 0.14673 | 4.5218 | 0 | 4.6685 |  | 15.0685 | 4 | 15.0685 | 69.1784 | 34.5892 | 15 | 35 | -0.41079 | -33.1739 | 0.010547 | -0.00010502 | -1 | 0
370 | 6.1667 | 4.9933 | 11.9893 | 5 | 12 | 69.282 | 40 | 0.010698 | 3.3529 | 0.00015108 | 0.14883 | 4.5363 | 0 | 4.6851 |  | 15.0851 | 4 | 15.0851 | 69.282 | 34.641 | 15 | 35 | -0.35899 | -33.5329 | 0.010698 | -9.4426e-05 | -1 | 0
371 | 6.1833 | 4.9932 | 11.9892 | 5 | 12 | 69.3853 | 40 | 0.010832 | 3.3637 | 0.00013414 | 0.15069 | 4.551 | 0 | 4.7016 |  | 15.1016 | 4 | 15.1016 | 69.3853 | 34.6926 | 15 | 35 | -0.30736 | -33.8402 | 0.010832 | -8.3835e-05 | -1 | 0
372 | 6.2 | 4.9932 | 11.9891 | 5 | 12 | 69.4881 | 40 | 0.01095 | 3.3747 | 0.00011722 | 0.15232 | 4.5658 | 0 | 4.7181 |  | 15.1181 | 4 | 15.1181 | 69.4881 | 34.744 | 15 | 35 | -0.25597 | -34.0962 | 0.01095 | -7.3264e-05 | -1 | 0
373 | 6.2167 | 4.9931 | 11.989 | 5 | 12 | 69.5902 | 40 | 0.01105 | 3.3857 | 0.00010036 | 0.15372 | 4.5807 | 0 | 4.7344 |  | 15.1344 | 4 | 15.1344 | 69.5902 | 34.7951 | 15 | 35 | -0.20489 | -34.3011 | 0.01105 | -6.2727e-05 | -1 | 0
374 | 6.2333 | 4.993 | 11.9889 | 5 | 12 | 69.6916 | 40 | 0.011133 | 3.3969 | 8.3583e-05 | 0.15488 | 4.5958 | 0 | 4.7507 |  | 15.1507 | 4 | 15.1507 | 69.6916 | 34.8458 | 15 | 35 | -0.15419 | -34.4553 | 0.011133 | -5.2239e-05 | -1 | 0
375 | 6.25 | 4.993 | 11.9888 | 5 | 12 | 69.7922 | 40 | 0.0112 | 3.4081 | 6.6903e-05 | 0.15581 | 4.6109 | 0 | 4.7667 |  | 15.1667 | 4 | 15.1667 | 69.7922 | 34.8961 | 15 | 35 | -0.10392 | -34.5592 | 0.0112 | -4.1814e-05 | -1 | 0
376 | 6.2667 | 4.993 | 11.9887 | 5 | 12 | 69.8917 | 40 | 0.011251 | 3.4193 | 5.0346e-05 | 0.15651 | 4.6262 | 0 | 4.7827 |  | 15.1827 | 4 | 15.1827 | 69.8917 | 34.9458 | 15 | 35 | -0.054166 | -34.6134 | 0.011251 | -3.1466e-05 | -1 | 0
377 | 6.2833 | 4.9929 | 11.9887 | 5 | 12 | 69.99 | 40 | 0.011285 | 3.4306 | 3.3934e-05 | 0.15699 | 4.6414 | 0 | 4.7984 |  | 15.1984 | 4 | 15.1984 | 69.99 | 34.995 | 15 | 35 | -0.0049803 | -34.6184 | 0.011285 | -2.1209e-05 | -1 | 0
378 | 6.3 | 4.9929 | 11.9887 | 5 | 12 | 70.0871 | 40 | 0.011302 | 3.4419 | 1.7687e-05 | 0.15723 | 4.6567 | 0 | 4.8139 |  | 15.2139 | 4 | 15.2139 | 70.0871 | 35.0436 | 15 | 35 | 0.043574 | -34.5748 | 0.011302 | -1.1054e-05 | -1 | 0
379 | 6.3167 | 4.9929 | 11.9887 | 5 | 12 | 70.1829 | 40 | 0.011304 | 3.4532 | 1.6262e-06 | 0.15726 | 4.672 | 0 | 4.8293 |  | 15.2293 | 4 | 15.2293 | 70.1829 | 35.0914 | 15 | 35 | 0.091437 | -34.4834 | 0.011304 | -1.0164e-06 | -1 | 0
380 | 6.3333 | 4.9929 | 11.9887 | 5 | 12 | 70.2771 | 40 | 0.01129 | 3.4645 | -1.4228e-05 | 0.15706 | 4.6873 | 0 | 4.8443 |  | 15.2443 | 4 | 15.2443 | 70.2771 | 35.1386 | 15 | 35 | 0.13855 | -34.3448 | 0.01129 | 8.8927e-06 | 1 | 2
381 | 6.35 | 4.993 | 11.9887 | 5 | 12 | 70.3697 | 40 | 0.01126 | 3.4758 | -2.9857e-05 | 0.15664 | 4.7025 | 0 | 4.8592 |  | 15.2592 | 4 | 15.2592 | 70.3697 | 35.1849 | 15 | 35 | 0.18486 | -34.1599 | 0.01126 | 1.8661e-05 | 1 | 0
382 | 6.3667 | 4.993 | 11.9888 | 5 | 12 | 70.4606 | 40 | 0.011215 | 3.487 | -4.5241e-05 | 0.15601 | 4.7177 | 0 | 4.8737 |  | 15.2737 | 4 | 15.2737 | 70.4606 | 35.2303 | 15 | 35 | 0.23031 | -33.9296 | 0.011215 | 2.8276e-05 | 1 | 0
383 | 6.3833 | 4.993 | 11.9888 | 5 | 12 | 70.5497 | 40 | 0.011154 | 3.4981 | -6.0362e-05 | 0.15517 | 4.7328 | 0 | 4.8879 |  | 15.2879 | 4 | 15.2879 | 70.5497 | 35.2748 | 15 | 35 | 0.27484 | -33.6548 | 0.011154 | 3.7726e-05 | 1 | 0
384 | 6.4 | 4.9931 | 11.9889 | 5 | 12 | 70.6368 | 40 | 0.011079 | 3.5092 | -7.5202e-05 | 0.15413 | 4.7478 | 0 | 4.9019 |  | 15.3019 | 4 | 15.3019 | 70.6368 | 35.3184 | 15 | 35 | 0.31841 | -33.3364 | 0.011079 | 4.7001e-05 | 1 | 0
385 | 6.4167 | 4.9931 | 11.989 | 5 | 12 | 70.722 | 40 | 0.010989 | 3.5202 | -8.9745e-05 | 0.15288 | 4.7626 | 0 | 4.9155 |  | 15.3155 | 4 | 15.3155 | 70.722 | 35.361 | 15 | 35 | 0.36098 | -32.9754 | 0.010989 | 5.609e-05 | 1 | 0
386 | 6.4333 | 4.9932 | 11.9891 | 5 | 12 | 70.805 | 40 | 0.010885 | 3.5311 | -0.00010397 | 0.15143 | 4.7774 | 0 | 4.9288 |  | 15.3288 | 4 | 15.3288 | 70.805 | 35.4025 | 15 | 35 | 0.40248 | -32.5729 | 0.010885 | 6.4983e-05 | 1 | 0
387 | 6.45 | 4.9933 | 11.9892 | 5 | 12 | 70.8858 | 40 | 0.010767 | 3.5419 | -0.00011787 | 0.14979 | 4.7919 | 0 | 4.9417 |  | 15.3417 | 4 | 15.3417 | 70.8858 | 35.4429 | 15 | 35 | 0.44288 | -32.13 | 0.010767 | 7.3668e-05 | 1 | 0
388 | 6.4667 | 4.9934 | 11.9894 | 5 | 12 | 70.9643 | 40 | 0.010636 | 3.5525 | -0.00013142 | 0.14796 | 4.8063 | 0 | 4.9543 |  | 15.3543 | 4 | 15.3543 | 70.9643 | 35.4821 | 15 | 35 | 0.48213 | -31.6479 | 0.010636 | 8.2138e-05 | 1 | 0
389 | 6.4833 | 4.9934 | 11.9895 | 5 | 12 | 71.0404 | 40 | 0.010491 | 3.563 | -0.00014461 | 0.14595 | 4.8205 | 0 | 4.9665 |  | 15.3665 | 4 | 15.3665 | 71.0404 | 35.5202 | 15 | 35 | 0.5202 | -31.1277 | 0.010491 | 9.0383e-05 | 1 | 0
390 | 6.5 | 4.9935 | 11.9897 | 5 | 12 | 71.1141 | 40 | 0.010334 | 3.5733 | -0.00015743 | 0.14376 | 4.8345 | 0 | 4.9783 |  | 15.3783 | 4 | 15.3783 | 71.1141 | 35.5571 | 15 | 35 | 0.55705 | -30.5707 | 0.010334 | 9.8395e-05 | 1 | 0
391 | 6.5167 | 4.9936 | 11.9898 | 5 | 12 | 71.1853 | 40 | 0.010164 | 3.5835 | -0.00016986 | 0.1414 | 4.8482 | 0 | 4.9896 |  | 15.3896 | 4 | 15.3896 | 71.1853 | 35.5926 | 15 | 35 | 0.59264 | -29.978 | 0.010164 | 0.00010616 | 1 | 0
392 | 6.5333 | 4.9938 | 11.99 | 5 | 12 | 71.2539 | 40 | 0.0099823 | 3.5935 | -0.00018189 | 0.13887 | 4.8618 | 0 | 5.0006 |  | 15.4006 | 4 | 15.4006 | 71.2539 | 35.6269 | 15 | 35 | 0.62694 | -29.3511 | 0.0099823 | 0.00011368 | 1 | 0
393 | 6.55 | 4.9939 | 11.9902 | 5 | 12 | 71.3198 | 40 | 0.0097887 | 3.6033 | -0.00019352 | 0.13618 | 4.875 | 0 | 5.0112 |  | 15.4112 | 4 | 15.4112 | 71.3198 | 35.6599 | 15 | 35 | 0.65991 | -28.6912 | 0.0097887 | 0.00012095 | 1 | 0
394 | 6.5667 | 4.994 | 11.9904 | 5 | 12 | 71.3831 | 40 | 0.009584 | 3.6128 | -0.00020471 | 0.13333 | 4.888 | 0 | 5.0213 |  | 15.4213 | 4 | 15.4213 | 71.3831 | 35.6915 | 15 | 35 | 0.69153 | -27.9996 | 0.009584 | 0.00012795 | 1 | 0
395 | 6.5833 | 4.9941 | 11.9906 | 5 | 12 | 71.4435 | 40 | 0.0093685 | 3.6222 | -0.00021548 | 0.13033 | 4.9006 | 0 | 5.031 |  | 15.431 | 4 | 15.431 | 71.4435 | 35.7218 | 15 | 35 | 0.72177 | -27.2779 | 0.0093685 | 0.00013468 | 1 | 0
396 | 6.6 | 4.9943 | 11.9909 | 5 | 12 | 71.5012 | 40 | 0.0091427 | 3.6314 | -0.00022581 | 0.12719 | 4.913 | 0 | 5.0402 |  | 15.4402 | 4 | 15.4402 | 71.5012 | 35.7506 | 15 | 35 | 0.75061 | -26.5273 | 0.0091427 | 0.00014113 | 1 | 0
397 | 6.6167 | 4.9944 | 11.9911 | 5 | 12 | 71.556 | 40 | 0.0089071 | 3.6403 | -0.00023568 | 0.12391 | 4.9251 | 0 | 5.049 |  | 15.449 | 4 | 15.449 | 71.556 | 35.778 | 15 | 35 | 0.77802 | -25.7492 | 0.0089071 | 0.0001473 | 1 | 0
398 | 6.6333 | 4.9946 | 11.9913 | 5 | 12 | 71.608 | 40 | 0.008662 | 3.6489 | -0.0002451 | 0.1205 | 4.9368 | 0 | 5.0573 |  | 15.4573 | 4 | 15.4573 | 71.608 | 35.804 | 15 | 35 | 0.80399 | -24.9452 | 0.008662 | 0.00015319 | 1 | 0
399 | 6.65 | 4.9947 | 11.9916 | 5 | 12 | 71.657 | 40 | 0.0084079 | 3.6573 | -0.00025405 | 0.11697 | 4.9482 | 0 | 5.0651 |  | 15.4651 | 4 | 15.4651 | 71.657 | 35.8285 | 15 | 35 | 0.8285 | -24.1167 | 0.0084079 | 0.00015878 | 1 | 0
400 | 6.6667 | 4.9949 | 11.9919 | 5 | 12 | 71.703 | 40 | 0.0081454 | 3.6655 | -0.00026253 | 0.11331 | 4.9592 | 0 | 5.0725 |  | 15.4725 | 4 | 15.4725 | 71.703 | 35.8515 | 15 | 35 | 0.85152 | -23.2652 | 0.0081454 | 0.00016408 | 1 | 0
401 | 6.6833 | 4.9951 | 11.9921 | 5 | 12 | 71.7461 | 40 | 0.0078749 | 3.6733 | -0.00027053 | 0.10955 | 4.9698 | 0 | 5.0794 |  | 15.4794 | 4 | 15.4794 | 71.7461 | 35.8731 | 15 | 35 | 0.87305 | -22.3922 | 0.0078749 | 0.00016908 | 1 | 0
402 | 6.7 | 4.9953 | 11.9924 | 5 | 12 | 71.7862 | 40 | 0.0075968 | 3.6809 | -0.00027805 | 0.10568 | 4.9801 | 0 | 5.0858 |  | 15.4858 | 4 | 15.4858 | 71.7862 | 35.8931 | 15 | 35 | 0.89308 | -21.4991 | 0.0075968 | 0.00017378 | 1 | 0
403 | 6.7167 | 4.9954 | 11.9927 | 5 | 12 | 71.8232 | 40 | 0.0073117 | 3.6883 | -0.00028508 | 0.10172 | 4.99 | 0 | 5.0917 |  | 15.4917 | 4 | 15.4917 | 71.8232 | 35.9116 | 15 | 35 | 0.91161 | -20.5875 | 0.0073117 | 0.00017817 | 1 | 0
404 | 6.7333 | 4.9956 | 11.993 | 5 | 12 | 71.8572 | 40 | 0.0070201 | 3.6953 | -0.00029162 | 0.097661 | 4.9995 | 0 | 5.0972 |  | 15.4972 | 4 | 15.4972 | 71.8572 | 35.9286 | 15 | 35 | 0.92861 | -19.6589 | 0.0070201 | 0.00018226 | 1 | 0
405 | 6.75 | 4.9958 | 11.9933 | 5 | 12 | 71.8882 | 40 | 0.0067224 | 3.702 | -0.00029767 | 0.09352 | 5.0086 | 0 | 5.1021 |  | 15.5021 | 4 | 15.5021 | 71.8882 | 35.9441 | 15 | 35 | 0.94409 | -18.7148 | 0.0067224 | 0.00018604 | 1 | 0
406 | 6.7667 | 4.996 | 11.9936 | 5 | 12 | 71.9161 | 40 | 0.0064192 | 3.7084 | -0.00030322 | 0.089301 | 5.0173 | 0 | 5.1066 |  | 15.5066 | 4 | 15.5066 | 71.9161 | 35.958 | 15 | 35 | 0.95805 | -17.7567 | 0.0064192 | 0.00018951 | 1 | 0
407 | 6.7833 | 4.9962 | 11.9939 | 5 | 12 | 71.941 | 40 | 0.0061109 | 3.7145 | -0.00030827 | 0.085013 | 5.0255 | 0 | 5.1106 |  | 15.5106 | 4 | 15.5106 | 71.941 | 35.9705 | 15 | 35 | 0.97048 | -16.7863 | 0.0061109 | 0.00019267 | 1 | 0
408 | 6.8 | 4.9964 | 11.9942 | 5 | 12 | 71.9628 | 40 | 0.0057981 | 3.7203 | -0.00031283 | 0.080661 | 5.0334 | 0 | 5.114 |  | 15.514 | 4 | 15.514 | 71.9628 | 35.9814 | 15 | 35 | 0.9814 | -15.8049 | 0.0057981 | 0.00019552 | 1 | 0
409 | 6.8167 | 4.9966 | 11.9945 | 5 | 12 | 71.9816 | 40 | 0.0054812 | 3.7258 | -0.00031689 | 0.076252 | 5.0408 | 0 | 5.1171 |  | 15.5171 | 4 | 15.5171 | 71.9816 | 35.9908 | 15 | 35 | 0.99079 | -14.8141 | 0.0054812 | 0.00019806 | 1 | 0
410 | 6.8333 | 4.9968 | 11.9948 | 5 | 12 | 71.9974 | 40 | 0.0051608 | 3.731 | -0.00032046 | 0.071794 | 5.0478 | 0 | 5.1196 |  | 15.5196 | 4 | 15.5196 | 71.9974 | 35.9987 | 15 | 35 | 0.99868 | -13.8154 | 0.0051608 | 0.00020028 | 1 | 0
411 | 6.85 | 4.997 | 11.9952 | 5 | 12 | 72.0101 | 40 | 0.0048372 | 3.7358 | -0.00032352 | 0.067294 | 5.0543 | 0 | 5.1216 |  | 15.5216 | 4 | 15.5216 | 72.0101 | 36.0051 | 15 | 35 | 1.0051 | -12.8103 | 0.0048372 | 0.0002022 | 1 | 0
412 | 6.8667 | 4.9972 | 11.9955 | 5 | 12 | 72.0199 | 40 | 0.0045111 | 3.7403 | -0.0003261 | 0.062757 | 5.0604 | 0 | 5.1232 |  | 15.5232 | 4 | 15.5232 | 72.0199 | 36.01 | 15 | 35 | 1.01 | -11.8003 | 0.0045111 | 0.00020381 | 1 | 0
413 | 6.8833 | 4.9974 | 11.9958 | 5 | 12 | 72.0268 | 40 | 0.004183 | 3.7445 | -0.00032819 | 0.058191 | 5.0661 | 0 | 5.1243 |  | 15.5243 | 4 | 15.5243 | 72.0268 | 36.0134 | 15 | 35 | 1.0134 | -10.787 | 0.004183 | 0.00020512 | 1 | 0
414 | 6.9 | 4.9976 | 11.9961 | 5 | 12 | 72.0307 | 40 | 0.0038532 | 3.7484 | -0.00032978 | 0.053604 | 5.0713 | 0 | 5.1249 |  | 15.5249 | 4 | 15.5249 | 72.0307 | 36.0153 | 15 | 35 | 1.0153 | -9.7716 | 0.0038532 | 0.00020612 | 1 | 0
415 | 6.9167 | 4.9978 | 11.9965 | 5 | 12 | 72.0317 | 40 | 0.0035223 | 3.7519 | -0.0003309 | 0.049 | 5.0761 | 0 | 5.1251 |  | 15.5251 | 4 | 15.5251 | 72.0317 | 36.0158 | 15 | 35 | 1.0158 | -8.7558 | 0.0035223 | 0.00020681 | 1 | 0
416 | 6.9333 | 4.998 | 11.9968 | 5 | 12 | 72.0298 | 40 | 0.0031907 | 3.7551 | -0.00033154 | 0.044388 | 5.0804 | 0 | 5.1248 |  | 15.5248 | 4 | 15.5248 | 72.0298 | 36.0149 | 15 | 35 | 1.0149 | -7.7409 | 0.0031907 | 0.00020721 | 1 | 0
417 | 6.95 | 4.9982 | 11.9971 | 5 | 12 | 72.0252 | 40 | 0.002859 | 3.7579 | -0.0003317 | 0.039774 | 5.0843 | 0 | 5.124 |  | 15.524 | 4 | 15.524 | 72.0252 | 36.0126 | 15 | 35 | 1.0126 | -6.7283 | 0.002859 | 0.00020732 | 1 | 0
418 | 6.9667 | 4.9984 | 11.9975 | 5 | 12 | 72.0177 | 40 | 0.0025276 | 3.7605 | -0.0003314 | 0.035163 | 5.0877 | 0 | 5.1228 |  | 15.5228 | 4 | 15.5228 | 72.0177 | 36.0089 | 15 | 35 | 1.0089 | -5.7194 | 0.0025276 | 0.00020713 | 1 | 0
419 | 6.9833 | 4.9986 | 11.9978 | 5 | 12 | 72.0076 | 40 | 0.002197 | 3.7627 | -0.00033064 | 0.030563 | 5.0906 | 0 | 5.1212 |  | 15.5212 | 4 | 15.5212 | 72.0076 | 36.0038 | 15 | 35 | 1.0038 | -4.7156 | 0.002197 | 0.00020665 | 1 | 0
420 | 7 | 4.9988 | 11.9981 | 5 | 12 | 71.9947 | 40 | 0.0018676 | 3.7645 | -0.00032943 | 0.025981 | 5.0932 | 0 | 5.1192 |  | 15.5192 | 4 | 15.5192 | 71.9947 | 35.9974 | 15 | 35 | 0.99736 | -3.7183 | 0.0018676 | 0.00020589 | 1 | 0
421 | 7.0167 | 4.999 | 11.9985 | 5 | 12 | 71.9792 | 40 | 0.0015398 | 3.7661 | -0.00032777 | 0.021421 | 5.0953 | 0 | 5.1167 |  | 15.5167 | 4 | 15.5167 | 71.9792 | 35.9896 | 15 | 35 | 0.98962 | -2.7286 | 0.0015398 | 0.00020485 | 1 | 0
422 | 7.0333 | 4.9992 | 11.9988 | 5 | 12 | 71.9612 | 40 | 0.0012141 | 3.7673 | -0.00032567 | 0.01689 | 5.0969 | 0 | 5.1138 |  | 15.5138 | 4 | 15.5138 | 71.9612 | 35.9806 | 15 | 35 | 0.98059 | -1.7481 | 0.0012141 | 0.00020354 | 1 | 0
423 | 7.05 | 4.9994 | 11.9991 | 5 | 12 | 71.9406 | 40 | 0.00089099 | 3.7682 | -0.00032314 | 0.012395 | 5.0981 | 0 | 5.1105 |  | 15.5105 | 4 | 15.5105 | 71.9406 | 35.9703 | 15 | 35 | 0.97031 | -0.77774 | 0.00089099 | 0.00020196 | 1 | 0
424 | 7.0667 | 4.9996 | 11.9994 | 5 | 12 | 71.9176 | 40 | 0.00057079 | 3.7687 | -0.00032019 | 0.0079406 | 5.0989 | 0 | 5.1068 |  | 15.5068 | 4 | 15.5068 | 71.9176 | 35.9588 | 15 | 35 | 0.95881 | 0.18106 | 0.00057079 | 0.00020012 | 1 | 0
425 | 7.0833 | 4.9998 | 11.9997 | 5 | 12 | 71.8922 | 40 | 0.00025396 | 3.769 | -0.00031684 | 0.0035329 | 5.0992 | 0 | 5.1028 |  | 15.5028 | 4 | 15.5028 | 71.8922 | 35.9461 | 15 | 35 | 0.94611 | 1.1272 | 0.00025396 | 0.00019802 | 1 | 0
426 | 7.1 | 5 | 12.0001 | 5 | 12 | 71.8645 | 40 | -5.9123e-05 | 3.7689 | -0.00031308 | -0.00082249 | 5.0991 | 0 | 5.0983 |  | 15.4983 | 4 | 15.4983 | 71.8645 | 35.9322 | 15 | 35 | 0.93224 | 2.0594 | 5.9123e-05 | 0.00019567 | 1 | 0
427 | 7.1167 | 5.0002 | 12.0004 | 5 | 12 | 71.8345 | 40 | -0.00036806 | 3.7686 | -0.00030893 | -0.0051202 | 5.0986 | 0 | 5.0935 |  | 15.4935 | 4 | 15.4935 | 71.8345 | 35.9173 | 15 | 35 | 0.91726 | 2.9767 | 0.00036806 | 0.00019308 | 1 | 0
428 | 7.1333 | 5.0004 | 12.0007 | 5 | 12 | 71.8024 | 40 | -0.00067246 | 3.7679 | -0.00030441 | -0.009355 | 5.0977 | 0 | 5.0884 |  | 15.4884 | 4 | 15.4884 | 71.8024 | 35.9012 | 15 | 35 | 0.90118 | 3.8779 | 0.00067246 | 0.00019025 | 1 | 0
429 | 7.15 | 5.0006 | 12.001 | 5 | 12 | 71.7681 | 40 | -0.00097197 | 3.7669 | -0.00029951 | -0.013522 | 5.0964 | 0 | 5.0829 |  | 15.4829 | 4 | 15.4829 | 71.7681 | 35.8841 | 15 | 35 | 0.88405 | 4.7619 | 0.00097197 | 0.0001872 | 1 | 0
430 | 7.1667 | 5.0008 | 12.0013 | 5 | 12 | 71.7318 | 40 | -0.0012662 | 3.7657 | -0.00029426 | -0.017615 | 5.0947 | 0 | 5.0771 |  | 15.4771 | 4 | 15.4771 | 71.7318 | 35.8659 | 15 | 35 | 0.8659 | 5.6278 | 0.0012662 | 0.00018391 | 1 | 0
431 | 7.1833 | 5.001 | 12.0016 | 5 | 12 | 71.6936 | 40 | -0.0015549 | 3.7641 | -0.00028867 | -0.021631 | 5.0926 | 0 | 5.071 |  | 15.471 | 4 | 15.471 | 71.6936 | 35.8468 | 15 | 35 | 0.84678 | 6.4746 | 0.0015549 | 0.00018042 | 1 | 0
432 | 7.2 | 5.0011 | 12.0018 | 5 | 12 | 71.6534 | 40 | -0.0018377 | 3.7623 | -0.00028274 | -0.025565 | 5.0901 | 0 | 5.0646 |  | 15.4646 | 4 | 15.4646 | 71.6534 | 35.8267 | 15 | 35 | 0.82672 | 7.3013 | 0.0018377 | 0.00017672 | 1 | 0
433 | 7.2167 | 5.0013 | 12.0021 | 5 | 12 | 71.6115 | 40 | -0.0021142 | 3.7601 | -0.0002765 | -0.029411 | 5.0873 | 0 | 5.0578 |  | 15.4578 | 4 | 15.4578 | 71.6115 | 35.8058 | 15 | 35 | 0.80576 | 8.1071 | 0.0021142 | 0.00017281 | 1 | 0
434 | 7.2333 | 5.0015 | 12.0024 | 5 | 12 | 71.5679 | 40 | -0.0023841 | 3.7578 | -0.00026995 | -0.033167 | 5.084 | 0 | 5.0509 |  | 15.4509 | 4 | 15.4509 | 71.5679 | 35.7839 | 15 | 35 | 0.78395 | 8.891 | 0.0023841 | 0.00016872 | 1 | 0
435 | 7.25 | 5.0017 | 12.0026 | 5 | 12 | 71.5226 | 40 | -0.0026472 | 3.7551 | -0.00026311 | -0.036827 | 5.0804 | 0 | 5.0436 |  | 15.4436 | 4 | 15.4436 | 71.5226 | 35.7613 | 15 | 35 | 0.76131 | 9.6523 | 0.0026472 | 0.00016444 | 1 | 0
436 | 7.2667 | 5.0018 | 12.0029 | 5 | 12 | 71.4758 | 40 | -0.0029032 | 3.7522 | -0.00025598 | -0.040388 | 5.0765 | 0 | 5.0361 |  | 15.4361 | 4 | 15.4361 | 71.4758 | 35.7379 | 15 | 35 | 0.73791 | 10.3902 | 0.0029032 | 0.00015999 | 1 | 0
437 | 7.2833 | 5.002 | 12.0032 | 5 | 12 | 71.4276 | 40 | -0.0031518 | 3.7491 | -0.00024859 | -0.043846 | 5.0723 | 0 | 5.0284 |  | 15.4284 | 4 | 15.4284 | 71.4276 | 35.7138 | 15 | 35 | 0.71378 | 11.104 | 0.0031518 | 0.00015537 | 1 | 0
438 | 7.3 | 5.0021 | 12.0034 | 5 | 12 | 71.3779 | 40 | -0.0033927 | 3.7457 | -0.00024095 | -0.047198 | 5.0677 | 0 | 5.0205 |  | 15.4205 | 4 | 15.4205 | 71.3779 | 35.689 | 15 | 35 | 0.68896 | 11.793 | 0.0033927 | 0.00015059 | 1 | 0
439 | 7.3167 | 5.0023 | 12.0036 | 5 | 12 | 71.327 | 40 | -0.0036258 | 3.742 | -0.00023307 | -0.050441 | 5.0628 | 0 | 5.0123 |  | 15.4123 | 4 | 15.4123 | 71.327 | 35.6635 | 15 | 35 | 0.6635 | 12.4565 | 0.0036258 | 0.00014567 | 1 | 0
440 | 7.3333 | 5.0024 | 12.0039 | 5 | 12 | 71.2749 | 40 | -0.0038508 | 3.7382 | -0.00022497 | -0.05357 | 5.0575 | 0 | 5.004 |  | 15.404 | 4 | 15.404 | 71.2749 | 35.6374 | 15 | 35 | 0.63744 | 13.0939 | 0.0038508 | 0.0001406 | 1 | 0
441 | 7.35 | 5.0025 | 12.0041 | 5 | 12 | 71.2216 | 40 | -0.0040674 | 3.7341 | -0.00021665 | -0.056584 | 5.052 | 0 | 4.9955 |  | 15.3955 | 4 | 15.3955 | 71.2216 | 35.6108 | 15 | 35 | 0.61082 | 13.7047 | 0.0040674 | 0.00013541 | 1 | 0
442 | 7.3667 | 5.0027 | 12.0043 | 5 | 12 | 71.1674 | 40 | -0.0042756 | 3.7298 | -0.00020814 | -0.05948 | 5.0463 | 0 | 4.9868 |  | 15.3868 | 4 | 15.3868 | 71.1674 | 35.5837 | 15 | 35 | 0.5837 | 14.2884 | 0.0042756 | 0.00013009 | 1 | 0
443 | 7.3833 | 5.0028 | 12.0045 | 5 | 12 | 71.1122 | 40 | -0.004475 | 3.7254 | -0.00019945 | -0.062254 | 5.0402 | 0 | 4.978 |  | 15.378 | 4 | 15.378 | 71.1122 | 35.5561 | 15 | 35 | 0.5561 | 14.8445 | 0.004475 | 0.00012466 | 1 | 0
444 | 7.4 | 5.0029 | 12.0047 | 5 | 12 | 71.0562 | 40 | -0.0046656 | 3.7207 | -0.00019059 | -0.064906 | 5.0339 | 0 | 4.969 |  | 15.369 | 4 | 15.369 | 71.0562 | 35.5281 | 15 | 35 | 0.52809 | 15.3726 | 0.0046656 | 0.00011912 | 1 | 0
445 | 7.4167 | 5.003 | 12.0048 | 5 | 12 | 70.9994 | 40 | -0.0048472 | 3.7159 | -0.00018159 | -0.067432 | 5.0273 | 0 | 4.9599 |  | 15.3599 | 4 | 15.3599 | 70.9994 | 35.4997 | 15 | 35 | 0.49971 | 15.8723 | 0.0048472 | 0.00011349 | 1 | 0
446 | 7.4333 | 5.0031 | 12.005 | 5 | 12 | 70.942 | 40 | -0.0050196 | 3.7108 | -0.00017244 | -0.069831 | 5.0205 | 0 | 4.9507 |  | 15.3507 | 4 | 15.3507 | 70.942 | 35.471 | 15 | 35 | 0.47099 | 16.3433 | 0.0050196 | 0.00010777 | 1 | 0
447 | 7.45 | 5.0032 | 12.0052 | 5 | 12 | 70.884 | 40 | -0.0051828 | 3.7057 | -0.00016317 | -0.072101 | 5.0135 | 0 | 4.9414 |  | 15.3414 | 4 | 15.3414 | 70.884 | 35.442 | 15 | 35 | 0.44198 | 16.7853 | 0.0051828 | 0.00010198 | 1 | 0
448 | 7.4667 | 5.0033 | 12.0053 | 5 | 12 | 70.8255 | 40 | -0.0053366 | 3.7003 | -0.00015379 | -0.07424 | 5.0063 | 0 | 4.9321 |  | 15.3321 | 4 | 15.3321 | 70.8255 | 35.4127 | 15 | 35 | 0.41273 | 17.198 | 0.0053366 | 9.612e-05 | 1 | 0
449 | 7.4833 | 5.0034 | 12.0055 | 5 | 12 | 70.7666 | 40 | -0.0054809 | 3.6948 | -0.00014432 | -0.076248 | 4.9989 | 0 | 4.9227 |  | 15.3227 | 4 | 15.3227 | 70.7666 | 35.3833 | 15 | 35 | 0.38328 | 17.5813 | 0.0054809 | 9.02e-05 | 1 | 0
450 | 7.5 | 5.0035 | 12.0056 | 5 | 12 | 70.7074 | 40 | -0.0056157 | 3.6892 | -0.00013477 | -0.078123 | 4.9913 | 0 | 4.9132 |  | 15.3132 | 4 | 15.3132 | 70.7074 | 35.3537 | 15 | 35 | 0.35368 | 17.935 | 0.0056157 | 8.4231e-05 | 1 | 0
451 | 7.5167 | 5.0036 | 12.0057 | 5 | 12 | 70.6479 | 40 | -0.0057408 | 3.6835 | -0.00012515 | -0.079864 | 4.9835 | 0 | 4.9037 |  | 15.3037 | 4 | 15.3037 | 70.6479 | 35.324 | 15 | 35 | 0.32397 | 18.259 | 0.0057408 | 7.8221e-05 | 1 | 0
452 | 7.5333 | 5.0037 | 12.0059 | 5 | 12 | 70.5884 | 40 | -0.0058563 | 3.6776 | -0.00011549 | -0.081471 | 4.9756 | 0 | 4.8941 |  | 15.2941 | 4 | 15.2941 | 70.5884 | 35.2942 | 15 | 35 | 0.29419 | 18.5532 | 0.0058563 | 7.218e-05 | 1 | 0
453 | 7.55 | 5.0037 | 12.006 | 5 | 12 | 70.5288 | 40 | -0.0059621 | 3.6717 | -0.00010579 | -0.082942 | 4.9675 | 0 | 4.8846 |  | 15.2846 | 4 | 15.2846 | 70.5288 | 35.2644 | 15 | 35 | 0.26438 | 18.8175 | 0.0059621 | 6.6116e-05 | 1 | 0
454 | 7.5667 | 5.0038 | 12.0061 | 5 | 12 | 70.4692 | 40 | -0.0060582 | 3.6656 | -9.6062e-05 | -0.084279 | 4.9593 | 0 | 4.8751 |  | 15.2751 | 4 | 15.2751 | 70.4692 | 35.2346 | 15 | 35 | 0.23459 | 19.0521 | 0.0060582 | 6.0038e-05 | 1 | 0
455 | 7.5833 | 5.0038 | 12.0061 | 5 | 12 | 70.4097 | 40 | -0.0061445 | 3.6595 | -8.6329e-05 | -0.08548 | 4.951 | 0 | 4.8656 |  | 15.2656 | 4 | 15.2656 | 70.4097 | 35.2049 | 15 | 35 | 0.20486 | 19.257 | 0.0061445 | 5.3956e-05 | 1 | 0
456 | 7.6 | 5.0039 | 12.0062 | 5 | 12 | 70.3505 | 40 | -0.0062211 | 3.6532 | -7.6602e-05 | -0.086545 | 4.9426 | 0 | 4.8561 |  | 15.2561 | 4 | 15.2561 | 70.3505 | 35.1752 | 15 | 35 | 0.17523 | 19.4322 | 0.0062211 | 4.7876e-05 | 1 | 0
457 | 7.6167 | 5.0039 | 12.0063 | 5 | 12 | 70.2915 | 40 | -0.006288 | 3.647 | -6.6893e-05 | -0.087476 | 4.9341 | 0 | 4.8466 |  | 15.2466 | 4 | 15.2466 | 70.2915 | 35.1457 | 15 | 35 | 0.14573 | 19.578 | 0.006288 | 4.1808e-05 | 1 | 0
458 | 7.6333 | 5.004 | 12.0063 | 5 | 12 | 70.2328 | 40 | -0.0063452 | 3.6406 | -5.7217e-05 | -0.088272 | 4.9255 | 0 | 4.8373 |  | 15.2373 | 4 | 15.2373 | 70.2328 | 35.1164 | 15 | 35 | 0.11642 | 19.6944 | 0.0063452 | 3.5761e-05 | 1 | 0
459 | 7.65 | 5.004 | 12.0064 | 5 | 12 | 70.1746 | 40 | -0.0063928 | 3.6342 | -4.7587e-05 | -0.088934 | 4.9169 | 0 | 4.8279 |  | 15.2279 | 4 | 15.2279 | 70.1746 | 35.0873 | 15 | 35 | 0.087323 | 19.7817 | 0.0063928 | 2.9742e-05 | 1 | 0
460 | 7.6667 | 5.004 | 12.0064 | 5 | 12 | 70.117 | 40 | -0.0064308 | 3.6278 | -3.8015e-05 | -0.089463 | 4.9082 | 0 | 4.8187 |  | 15.2187 | 4 | 15.2187 | 70.117 | 35.0585 | 15 | 35 | 0.058481 | 19.8402 | 0.0064308 | 2.3759e-05 | 1 | 0
461 | 7.6833 | 5.004 | 12.0065 | 5 | 12 | 70.0599 | 40 | -0.0064593 | 3.6213 | -2.8514e-05 | -0.089859 | 4.8994 | 0 | 4.8096 |  | 15.2096 | 4 | 15.2096 | 70.0599 | 35.0299 | 15 | 35 | 0.029932 | 19.8701 | 0.0064593 | 1.7821e-05 | 1 | 0
462 | 7.7 | 5.004 | 12.0065 | 5 | 12 | 70.0034 | 40 | -0.0064784 | 3.6148 | -1.9096e-05 | -0.090125 | 4.8907 | 0 | 4.8005 |  | 15.2005 | 4 | 15.2005 | 70.0034 | 35.0017 | 15 | 35 | 0.0017115 | 19.8718 | 0.0064784 | 1.1935e-05 | 1 | 0
463 | 7.7167 | 5.0041 | 12.0065 | 5 | 12 | 69.9477 | 40 | -0.0064882 | 3.6084 | -9.7737e-06 | -0.090261 | 4.8819 | 0 | 4.7916 |  | 15.1916 | 4 | 15.1916 | 69.9477 | 34.9739 | 15 | 35 | -0.026145 | 19.8457 | 0.0064882 | 6.1086e-06 | 1 | 0
464 | 7.7333 | 5.0041 | 12.0065 | 5 | 12 | 69.8928 | 40 | -0.0064888 | 3.6019 | -5.5885e-07 | -0.090269 | 4.8731 | 0 | 4.7828 |  | 15.1828 | 4 | 15.1828 | 69.8928 | 34.9464 | 15 | 35 | -0.053604 | 19.7921 | 0.0064888 | 3.4928e-07 | 1 | 0
465 | 7.75 | 5.0041 | 12.0065 | 5 | 12 | 69.8387 | 40 | -0.0064802 | 3.5954 | 8.5372e-06 | -0.09015 | 4.8643 | 0 | 4.7742 |  | 15.1742 | 4 | 15.1742 | 69.8387 | 34.9194 | 15 | 35 | -0.08063 | 19.7114 | 0.0064802 | -5.3357e-06 | -1 | -2
466 | 7.7667 | 5.004 | 12.0065 | 5 | 12 | 69.7856 | 40 | -0.0064627 | 3.5889 | 1.7503e-05 | -0.089906 | 4.8556 | 0 | 4.7657 |  | 15.1657 | 4 | 15.1657 | 69.7856 | 34.8928 | 15 | 35 | -0.10719 | 19.6042 | 0.0064627 | -1.0939e-05 | -1 | 0
467 | 7.7833 | 5.004 | 12.0064 | 5 | 12 | 69.7335 | 40 | -0.0064364 | 3.5825 | 2.6328e-05 | -0.08954 | 4.8469 | 0 | 4.7574 |  | 15.1574 | 4 | 15.1574 | 69.7335 | 34.8667 | 15 | 35 | -0.13326 | 19.471 | 0.0064364 | -1.6455e-05 | -1 | 0
468 | 7.8 | 5.004 | 12.0064 | 5 | 12 | 69.6824 | 40 | -0.0064014 | 3.5761 | 3.5002e-05 | -0.089053 | 4.8382 | 0 | 4.7492 |  | 15.1492 | 4 | 15.1492 | 69.6824 | 34.8412 | 15 | 35 | -0.1588 | 19.3122 | 0.0064014 | -2.1876e-05 | -1 | 0
469 | 7.8167 | 5.004 | 12.0064 | 5 | 12 | 69.6324 | 40 | -0.0063579 | 3.5697 | 4.3514e-05 | -0.088448 | 4.8296 | 0 | 4.7412 |  | 15.1412 | 4 | 15.1412 | 69.6324 | 34.8162 | 15 | 35 | -0.18379 | 19.1284 | 0.0063579 | -2.7196e-05 | -1 | 0
470 | 7.8333 | 5.0039 | 12.0063 | 5 | 12 | 69.5836 | 40 | -0.006306 | 3.5634 | 5.1855e-05 | -0.087727 | 4.8211 | 0 | 4.7334 |  | 15.1334 | 4 | 15.1334 | 69.5836 | 34.7918 | 15 | 35 | -0.2082 | 18.9202 | 0.006306 | -3.2409e-05 | -1 | 0
471 | 7.85 | 5.0039 | 12.0062 | 5 | 12 | 69.536 | 40 | -0.006246 | 3.5572 | 6.0014e-05 | -0.086892 | 4.8127 | 0 | 4.7258 |  | 15.1258 | 4 | 15.1258 | 69.536 | 34.768 | 15 | 35 | -0.232 | 18.6882 | 0.006246 | -3.7509e-05 | -1 | 0
472 | 7.8667 | 5.0039 | 12.0062 | 5 | 12 | 69.4897 | 40 | -0.006178 | 3.551 | 6.7984e-05 | -0.085946 | 4.8043 | 0 | 4.7183 |  | 15.1183 | 4 | 15.1183 | 69.4897 | 34.7448 | 15 | 35 | -0.25516 | 18.433 | 0.006178 | -4.249e-05 | -1 | 0
473 | 7.8833 | 5.0038 | 12.0061 | 5 | 12 | 69.4447 | 40 | -0.0061023 | 3.5449 | 7.5755e-05 | -0.084892 | 4.796 | 0 | 4.7111 |  | 15.1111 | 4 | 15.1111 | 69.4447 | 34.7223 | 15 | 35 | -0.27767 | 18.1554 | 0.0061023 | -4.7347e-05 | -1 | 0
474 | 7.9 | 5.0038 | 12.006 | 5 | 12 | 69.401 | 40 | -0.0060189 | 3.5389 | 8.3319e-05 | -0.083733 | 4.7879 | 0 | 4.7042 |  | 15.1042 | 4 | 15.1042 | 69.401 | 34.7005 | 15 | 35 | -0.2995 | 17.8559 | 0.0060189 | -5.2074e-05 | -1 | 0
475 | 7.9167 | 5.0037 | 12.0059 | 5 | 12 | 69.3588 | 40 | -0.0059283 | 3.5329 | 9.0668e-05 | -0.082472 | 4.7799 | 0 | 4.6974 |  | 15.0974 | 4 | 15.0974 | 69.3588 | 34.6794 | 15 | 35 | -0.32062 | 17.5352 | 0.0059283 | -5.6668e-05 | -1 | 0
476 | 7.9333 | 5.0036 | 12.0058 | 5 | 12 | 69.318 | 40 | -0.0058305 | 3.5271 | 9.7795e-05 | -0.081111 | 4.772 | 0 | 4.6909 |  | 15.0909 | 4 | 15.0909 | 69.318 | 34.659 | 15 | 35 | -0.34102 | 17.1942 | 0.0058305 | -6.1122e-05 | -1 | 0
477 | 7.95 | 5.0036 | 12.0057 | 5 | 12 | 69.2786 | 40 | -0.0057258 | 3.5214 | 0.00010469 | -0.079655 | 4.7642 | 0 | 4.6846 |  | 15.0846 | 4 | 15.0846 | 69.2786 | 34.6393 | 15 | 35 | -0.36068 | 16.8335 | 0.0057258 | -6.5432e-05 | -1 | 0
478 | 7.9667 | 5.0035 | 12.0056 | 5 | 12 | 69.2409 | 40 | -0.0056144 | 3.5158 | 0.00011135 | -0.078106 | 4.7566 | 0 | 4.6785 |  | 15.0785 | 4 | 15.0785 | 69.2409 | 34.6204 | 15 | 35 | -0.37957 | 16.454 | 0.0056144 | -6.9596e-05 | -1 | 0
479 | 7.9833 | 5.0034 | 12.0055 | 5 | 12 | 69.2046 | 40 | -0.0054967 | 3.5103 | 0.00011777 | -0.076467 | 4.7492 | 0 | 4.6727 |  | 15.0727 | 4 | 15.0727 | 69.2046 | 34.6023 | 15 | 35 | -0.39769 | 16.0563 | 0.0054967 | -7.3607e-05 | -1 | 0
480 | 8 | 5.0034 | 12.0054 | 5 | 12 | 69.17 | 40 | -0.0053727 | 3.5049 | 0.00012394 | -0.074743 | 4.7419 | 0 | 4.6672 |  | 15.0672 | 4 | 15.0672 | 69.17 | 34.585 | 15 | 35 | -0.41502 | 15.6413 | 0.0053727 | -7.7464e-05 | -1 | 0
481 | 8.0167 | 5.0033 | 12.0052 | 5 | 12 | 69.1369 | 40 | -0.0052429 | 3.4997 | 0.00012986 | -0.072936 | 4.7348 | 0 | 4.6619 |  | 15.0619 | 4 | 15.0619 | 69.1369 | 34.5685 | 15 | 35 | -0.43154 | 15.2097 | 0.0052429 | -8.1162e-05 | -1 | 0
482 | 8.0333 | 5.0032 | 12.0051 | 5 | 12 | 69.1055 | 40 | -0.0051073 | 3.4946 | 0.00013552 | -0.071051 | 4.7279 | 0 | 4.6569 |  | 15.0569 | 4 | 15.0569 | 69.1055 | 34.5528 | 15 | 35 | -0.44724 | 14.7625 | 0.0051073 | -8.4698e-05 | -1 | 0
483 | 8.05 | 5.0031 | 12.005 | 5 | 12 | 69.0758 | 40 | -0.0049664 | 3.4896 | 0.00014091 | -0.069091 | 4.7212 | 0 | 4.6521 |  | 15.0521 | 4 | 15.0521 | 69.0758 | 34.5379 | 15 | 35 | -0.46211 | 14.3004 | 0.0049664 | -8.8069e-05 | -1 | 0
484 | 8.0667 | 5.003 | 12.0048 | 5 | 12 | 69.0477 | 40 | -0.0048204 | 3.4848 | 0.00014604 | -0.067059 | 4.7147 | 0 | 4.6476 |  | 15.0476 | 4 | 15.0476 | 69.0477 | 34.5239 | 15 | 35 | -0.47615 | 13.8242 | 0.0048204 | -9.1274e-05 | -1 | 0
485 | 8.0833 | 5.0029 | 12.0047 | 5 | 12 | 69.0213 | 40 | -0.0046695 | 3.4801 | 0.00015089 | -0.06496 | 4.7084 | 0 | 4.6434 |  | 15.0434 | 4 | 15.0434 | 69.0213 | 34.5107 | 15 | 35 | -0.48933 | 13.3349 | 0.0046695 | -9.4309e-05 | -1 | 0
486 | 8.1 | 5.0028 | 12.0045 | 5 | 12 | 68.9967 | 40 | -0.004514 | 3.4756 | 0.00015548 | -0.062797 | 4.7023 | 0 | 4.6395 |  | 15.0395 | 4 | 15.0395 | 68.9967 | 34.4983 | 15 | 35 | -0.50165 | 12.8332 | 0.004514 | -9.7173e-05 | -1 | 0
487 | 8.1167 | 5.0027 | 12.0044 | 5 | 12 | 68.9738 | 40 | -0.0043542 | 3.4712 | 0.00015978 | -0.060574 | 4.6964 | 0 | 4.6358 |  | 15.0358 | 4 | 15.0358 | 68.9738 | 34.4869 | 15 | 35 | -0.51312 | 12.3201 | 0.0043542 | -9.9863e-05 | -1 | 0
488 | 8.1333 | 5.0026 | 12.0042 | 5 | 12 | 68.9526 | 40 | -0.0041904 | 3.467 | 0.00016381 | -0.058296 | 4.6907 | 0 | 4.6324 |  | 15.0324 | 4 | 15.0324 | 68.9526 | 34.4763 | 15 | 35 | -0.52371 | 11.7964 | 0.0041904 | -0.00010238 | -1 | 0
489 | 8.15 | 5.0025 | 12.004 | 5 | 12 | 68.9331 | 40 | -0.0040229 | 3.463 | 0.00016755 | -0.055965 | 4.6853 | 0 | 4.6293 |  | 15.0293 | 4 | 15.0293 | 68.9331 | 34.4666 | 15 | 35 | -0.53344 | 11.263 | 0.0040229 | -0.00010472 | -1 | 0
490 | 8.1667 | 5.0024 | 12.0039 | 5 | 12 | 68.9154 | 40 | -0.0038519 | 3.4592 | 0.00017101 | -0.053586 | 4.6801 | 0 | 4.6265 |  | 15.0265 | 4 | 15.0265 | 68.9154 | 34.4577 | 15 | 35 | -0.54229 | 10.7207 | 0.0038519 | -0.00010688 | -1 | 0
491 | 8.1833 | 5.0023 | 12.0037 | 5 | 12 | 68.8995 | 40 | -0.0036777 | 3.4555 | 0.00017418 | -0.051163 | 4.6751 | 0 | 4.6239 |  | 15.0239 | 4 | 15.0239 | 68.8995 | 34.4497 | 15 | 35 | -0.55027 | 10.1704 | 0.0036777 | -0.00010886 | -1 | 0
492 | 8.2 | 5.0022 | 12.0035 | 5 | 12 | 68.8853 | 40 | -0.0035006 | 3.452 | 0.00017707 | -0.048699 | 4.6703 | 0 | 4.6216 |  | 15.0216 | 4 | 15.0216 | 68.8853 | 34.4426 | 15 | 35 | -0.55737 | 9.613 | 0.0035006 | -0.00011067 | -1 | 0
493 | 8.2167 | 5.0021 | 12.0033 | 5 | 12 | 68.8728 | 40 | -0.0033209 | 3.4487 | 0.00017968 | -0.0462 | 4.6658 | 0 | 4.6196 |  | 15.0196 | 4 | 15.0196 | 68.8728 | 34.4364 | 15 | 35 | -0.5636 | 9.0494 | 0.0033209 | -0.0001123 | -1 | 0
494 | 8.2333 | 5.002 | 12.0031 | 5 | 12 | 68.8621 | 40 | -0.003139 | 3.4455 | 0.000182 | -0.043668 | 4.6616 | 0 | 4.6179 |  | 15.0179 | 4 | 15.0179 | 68.8621 | 34.431 | 15 | 35 | -0.56896 | 8.4805 | 0.003139 | -0.00011375 | -1 | 0
495 | 8.25 | 5.0018 | 12.003 | 5 | 12 | 68.8531 | 40 | -0.0029549 | 3.4426 | 0.00018403 | -0.041108 | 4.6576 | 0 | 4.6165 |  | 15.0165 | 4 | 15.0165 | 68.8531 | 34.4266 | 15 | 35 | -0.57345 | 7.907 | 0.0029549 | -0.00011502 | -1 | 0
496 | 8.2667 | 5.0017 | 12.0028 | 5 | 12 | 68.8458 | 40 | -0.0027691 | 3.4398 | 0.00018578 | -0.038523 | 4.6539 | 0 | 4.6153 |  | 15.0153 | 4 | 15.0153 | 68.8458 | 34.4229 | 15 | 35 | -0.57708 | 7.33 | 0.0027691 | -0.00011611 | -1 | 0
497 | 8.2833 | 5.0016 | 12.0026 | 5 | 12 | 68.8403 | 40 | -0.0025819 | 3.4372 | 0.00018725 | -0.035918 | 4.6504 | 0 | 4.6144 |  | 15.0144 | 4 | 15.0144 | 68.8403 | 34.4201 | 15 | 35 | -0.57986 | 6.7501 | 0.0025819 | -0.00011703 | -1 | 0
498 | 8.3 | 5.0015 | 12.0024 | 5 | 12 | 68.8364 | 40 | -0.0023935 | 3.4348 | 0.00018843 | -0.033297 | 4.6471 | 0 | 4.6138 |  | 15.0138 | 4 | 15.0138 | 68.8364 | 34.4182 | 15 | 35 | -0.58178 | 6.1683 | 0.0023935 | -0.00011777 | -1 | 0
499 | 8.3167 | 5.0014 | 12.0022 | 5 | 12 | 68.8343 | 40 | -0.0022041 | 3.4326 | 0.00018934 | -0.030663 | 4.6441 | 0 | 4.6135 |  | 15.0135 | 4 | 15.0135 | 68.8343 | 34.4171 | 15 | 35 | -0.58287 | 5.5854 | 0.0022041 | -0.00011834 | -1 | 0
500 | 8.3333 | 5.0013 | 12.002 | 5 | 12 | 68.8337 | 40 | -0.0020141 | 3.4306 | 0.00018997 | -0.02802 | 4.6414 | 0 | 4.6134 |  | 15.0134 | 4 | 15.0134 | 68.8337 | 34.4169 | 15 | 35 | -0.58313 | 5.0023 | 0.0020141 | -0.00011873 | -1 | 0
501 | 8.35 | 5.0011 | 12.0018 | 5 | 12 | 68.8349 | 40 | -0.0018238 | 3.4288 | 0.00019033 | -0.025372 | 4.639 | 0 | 4.6136 |  | 15.0136 | 4 | 15.0136 | 68.8349 | 34.4174 | 15 | 35 | -0.58257 | 4.4197 | 0.0018238 | -0.00011895 | -1 | 0
502 | 8.3667 | 5.001 | 12.0016 | 5 | 12 | 68.8376 | 40 | -0.0016334 | 3.4272 | 0.00019041 | -0.022723 | 4.6367 | 0 | 4.614 |  | 15.014 | 4 | 15.014 | 68.8376 | 34.4188 | 15 | 35 | -0.58119 | 3.8386 | 0.0016334 | -0.00011901 | -1 | 0
503 | 8.3833 | 5.0009 | 12.0014 | 5 | 12 | 68.8419 | 40 | -0.0014432 | 3.4257 | 0.00019023 | -0.020077 | 4.6348 | 0 | 4.6147 |  | 15.0147 | 4 | 15.0147 | 68.8419 | 34.421 | 15 | 35 | -0.57903 | 3.2595 | 0.0014432 | -0.00011889 | -1 | 0
504 | 8.4 | 5.0008 | 12.0013 | 5 | 12 | 68.8479 | 40 | -0.0012534 | 3.4245 | 0.00018978 | -0.017437 | 4.6331 | 0 | 4.6157 |  | 15.0157 | 4 | 15.0157 | 68.8479 | 34.4239 | 15 | 35 | -0.57607 | 2.6835 | 0.0012534 | -0.00011861 | -1 | 0
505 | 8.4167 | 5.0007 | 12.0011 | 5 | 12 | 68.8553 | 40 | -0.0010643 | 3.4234 | 0.00018907 | -0.014807 | 4.6317 | 0 | 4.6168 |  | 15.0168 | 4 | 15.0168 | 68.8553 | 34.4276 | 15 | 35 | -0.57235 | 2.1111 | 0.0010643 | -0.00011817 | -1 | 0
506 | 8.4333 | 5.0005 | 12.0009 | 5 | 12 | 68.8642 | 40 | -0.00087623 | 3.4225 | 0.00018811 | -0.01219 | 4.6305 | 0 | 4.6183 |  | 15.0183 | 4 | 15.0183 | 68.8642 | 34.4321 | 15 | 35 | -0.56788 | 1.5432 | 0.00087623 | -0.00011757 | -1 | 0
507 | 8.45 | 5.0004 | 12.0007 | 5 | 12 | 68.8747 | 40 | -0.00068934 | 3.4218 | 0.00018689 | -0.0095898 | 4.6295 | 0 | 4.6199 |  | 15.0199 | 4 | 15.0199 | 68.8747 | 34.4373 | 15 | 35 | -0.56267 | 0.98055 | 0.00068934 | -0.00011681 | -1 | 0
508 | 8.4667 | 5.0003 | 12.0005 | 5 | 12 | 68.8865 | 40 | -0.00050391 | 3.4213 | 0.00018543 | -0.0070102 | 4.6289 | 0 | 4.6218 |  | 15.0218 | 4 | 15.0218 | 68.8865 | 34.4433 | 15 | 35 | -0.55674 | 0.42381 | 0.00050391 | -0.00011589 | -1 | 0
509 | 8.4833 | 5.0002 | 12.0003 | 5 | 12 | 68.8998 | 40 | -0.00032018 | 3.421 | 0.00018373 | -0.0044542 | 4.6284 | 0 | 4.624 |  | 15.024 | 4 | 15.024 | 68.8998 | 34.4499 | 15 | 35 | -0.55011 | -0.1263 | 0.00032018 | -0.00011483 | -1 | 0
510 | 8.5 | 5.0001 | 12.0001 | 5 | 12 | 68.9144 | 40 | -0.00013839 | 3.4209 | 0.00018179 | -0.0019252 | 4.6282 | 0 | 4.6263 |  | 15.0263 | 4 | 15.0263 | 68.9144 | 34.4572 | 15 | 35 | -0.54279 | -0.66909 | 0.00013839 | -0.00011362 | -1 | 0
511 | 8.5167 | 5 | 12 | 5 | 12 | 68.9304 | 40 | 4.1241e-05 | 3.4209 | 0.00017963 | 0.00057372 | 4.6283 | 0 | 4.6289 |  | 15.0289 | 4 | 15.0289 | 68.9304 | 34.4652 | 15 | 35 | -0.53481 | -1.2039 | 4.1241e-05 | -0.00011227 | -1 | 0
512 | 8.5333 | 4.9999 | 11.9998 | 5 | 12 | 68.9476 | 40 | 0.00021848 | 3.4211 | 0.00017724 | 0.0030394 | 4.6286 | 0 | 4.6316 |  | 15.0316 | 4 | 15.0316 | 68.9476 | 34.4738 | 15 | 35 | -0.52618 | -1.7301 | 0.00021848 | -0.00011077 | -1 | 0
513 | 8.55 | 4.9998 | 11.9996 | 5 | 12 | 68.9662 | 40 | 0.00039311 | 3.4215 | 0.00017463 | 0.0054687 | 4.6291 | 0 | 4.6346 |  | 15.0346 | 4 | 15.0346 | 68.9662 | 34.4831 | 15 | 35 | -0.51692 | -2.247 | 0.00039311 | -0.00010914 | -1 | 0
514 | 8.5667 | 4.9996 | 11.9994 | 5 | 12 | 68.9859 | 40 | 0.00056492 | 3.4221 | 0.00017181 | 0.0078589 | 4.6299 | 0 | 4.6377 |  | 15.0377 | 4 | 15.0377 | 68.9859 | 34.4929 | 15 | 35 | -0.50706 | -2.7541 | 0.00056492 | -0.00010738 | -1 | 0
515 | 8.5833 | 4.9995 | 11.9993 | 5 | 12 | 69.0068 | 40 | 0.00073371 | 3.4228 | 0.00016879 | 0.010207 | 4.6309 | 0 | 4.6411 |  | 15.0411 | 4 | 15.0411 | 69.0068 | 34.5034 | 15 | 35 | -0.49662 | -3.2507 | 0.00073371 | -0.00010549 | -1 | 0
516 | 8.6 | 4.9994 | 11.9991 | 5 | 12 | 69.0288 | 40 | 0.00089928 | 3.4237 | 0.00016557 | 0.01251 | 4.6321 | 0 | 4.6446 |  | 15.0446 | 4 | 15.0446 | 69.0288 | 34.5144 | 15 | 35 | -0.48562 | -3.7363 | 0.00089928 | -0.00010348 | -1 | 0
517 | 8.6167 | 4.9993 | 11.9989 | 5 | 12 | 69.0518 | 40 | 0.0010614 | 3.4248 | 0.00016216 | 0.014766 | 4.6335 | 0 | 4.6483 |  | 15.0483 | 4 | 15.0483 | 69.0518 | 34.5259 | 15 | 35 | -0.47409 | -4.2104 | 0.0010614 | -0.00010135 | -1 | 0
518 | 8.6333 | 4.9992 | 11.9988 | 5 | 12 | 69.0759 | 40 | 0.00122 | 3.426 | 0.00015857 | 0.016972 | 4.6352 | 0 | 4.6521 |  | 15.0521 | 4 | 15.0521 | 69.0759 | 34.538 | 15 | 35 | -0.46204 | -4.6724 | 0.00122 | -9.9107e-05 | -1 | 0
519 | 8.65 | 4.9991 | 11.9986 | 5 | 12 | 69.101 | 40 | 0.0013748 | 3.4274 | 0.0001548 | 0.019126 | 4.637 | 0 | 4.6562 |  | 15.0562 | 4 | 15.0562 | 69.101 | 34.5505 | 15 | 35 | -0.44949 | -5.1219 | 0.0013748 | -9.6752e-05 | -1 | 0
520 | 8.6667 | 4.999 | 11.9985 | 5 | 12 | 69.127 | 40 | 0.0015257 | 3.4289 | 0.00015087 | 0.021225 | 4.6391 | 0 | 4.6603 |  | 15.0603 | 4 | 15.0603 | 69.127 | 34.5635 | 15 | 35 | -0.43648 | -5.5584 | 0.0015257 | -9.4293e-05 | -1 | 0
521 | 8.6833 | 4.999 | 11.9983 | 5 | 12 | 69.1539 | 40 | 0.0016725 | 3.4306 | 0.00014677 | 0.023267 | 4.6414 | 0 | 4.6646 |  | 15.0646 | 4 | 15.0646 | 69.1539 | 34.577 | 15 | 35 | -0.42303 | -5.9814 | 0.0016725 | -9.1733e-05 | -1 | 0
522 | 8.7 | 4.9989 | 11.9982 | 5 | 12 | 69.1817 | 40 | 0.001815 | 3.4324 | 0.00014253 | 0.025249 | 4.6438 | 0 | 4.6691 |  | 15.0691 | 4 | 15.0691 | 69.1817 | 34.5908 | 15 | 35 | -0.40916 | -6.3906 | 0.001815 | -8.9078e-05 | -1 | 0
523 | 8.7167 | 4.9988 | 11.998 | 5 | 12 | 69.2102 | 40 | 0.0019531 | 3.4343 | 0.00013813 | 0.027171 | 4.6465 | 0 | 4.6736 |  | 15.0736 | 4 | 15.0736 | 69.2102 | 34.6051 | 15 | 35 | -0.3949 | -6.7855 | 0.0019531 | -8.6333e-05 | -1 | 0
524 | 8.7333 | 4.9987 | 11.9979 | 5 | 12 | 69.2395 | 40 | 0.0020867 | 3.4364 | 0.0001336 | 0.02903 | 4.6493 | 0 | 4.6783 |  | 15.0783 | 4 | 15.0783 | 69.2395 | 34.6197 | 15 | 35 | -0.38027 | -7.1658 | 0.0020867 | -8.3502e-05 | -1 | 0
525 | 8.75 | 4.9986 | 11.9978 | 5 | 12 | 69.2694 | 40 | 0.0022157 | 3.4386 | 0.00012895 | 0.030823 | 4.6523 | 0 | 4.6831 |  | 15.0831 | 4 | 15.0831 | 69.2694 | 34.6347 | 15 | 35 | -0.36529 | -7.5311 | 0.0022157 | -8.0592e-05 | -1 | 0
526 | 8.7667 | 4.9985 | 11.9977 | 5 | 12 | 69.3 | 40 | 0.0023398 | 3.441 | 0.00012417 | 0.032551 | 4.6554 | 0 | 4.688 |  | 15.088 | 4 | 15.088 | 69.3 | 34.65 | 15 | 35 | -0.35 | -7.8811 | 0.0023398 | -7.7606e-05 | -1 | 0
527 | 8.7833 | 4.9985 | 11.9975 | 5 | 12 | 69.3312 | 40 | 0.0024591 | 3.4434 | 0.00011928 | 0.03421 | 4.6588 | 0 | 4.693 |  | 15.093 | 4 | 15.093 | 69.3312 | 34.6656 | 15 | 35 | -0.33442 | -8.2155 | 0.0024591 | -7.455e-05 | -1 | 0
528 | 8.8 | 4.9984 | 11.9974 | 5 | 12 | 69.3629 | 40 | 0.0025734 | 3.446 | 0.00011429 | 0.0358 | 4.6623 | 0 | 4.6981 |  | 15.0981 | 4 | 15.0981 | 69.3629 | 34.6814 | 15 | 35 | -0.31857 | -8.5341 | 0.0025734 | -7.1429e-05 | -1 | 0
529 | 8.8167 | 4.9983 | 11.9973 | 5 | 12 | 69.395 | 40 | 0.0026826 | 3.4487 | 0.0001092 | 0.037319 | 4.6659 | 0 | 4.7032 |  | 15.1032 | 4 | 15.1032 | 69.395 | 34.6975 | 15 | 35 | -0.30248 | -8.8365 | 0.0026826 | -6.8249e-05 | -1 | 0
530 | 8.8333 | 4.9983 | 11.9972 | 5 | 12 | 69.4276 | 40 | 0.0027866 | 3.4515 | 0.00010402 | 0.038766 | 4.6697 | 0 | 4.7084 |  | 15.1084 | 4 | 15.1084 | 69.4276 | 34.7138 | 15 | 35 | -0.28618 | -9.1227 | 0.0027866 | -6.5015e-05 | -1 | 0
531 | 8.85 | 4.9982 | 11.9971 | 5 | 12 | 69.4606 | 40 | 0.0028854 | 3.4544 | 9.877e-05 | 0.04014 | 4.6736 | 0 | 4.7137 |  | 15.1137 | 4 | 15.1137 | 69.4606 | 34.7303 | 15 | 35 | -0.26969 | -9.3924 | 0.0028854 | -6.1731e-05 | -1 | 0
532 | 8.8667 | 4.9981 | 11.997 | 5 | 12 | 69.4939 | 40 | 0.0029788 | 3.4573 | 9.3446e-05 | 0.04144 | 4.6776 | 0 | 4.719 |  | 15.119 | 4 | 15.119 | 69.4939 | 34.747 | 15 | 35 | -0.25303 | -9.6454 | 0.0029788 | -5.8404e-05 | -1 | 0
533 | 8.8833 | 4.9981 | 11.9969 | 5 | 12 | 69.5275 | 40 | 0.0030669 | 3.4604 | 8.8061e-05 | 0.042665 | 4.6817 | 0 | 4.7244 |  | 15.1244 | 4 | 15.1244 | 69.5275 | 34.7638 | 15 | 35 | -0.23623 | -9.8817 | 0.0030669 | -5.5038e-05 | -1 | 0
534 | 8.9 | 4.998 | 11.9969 | 5 | 12 | 69.5613 | 40 | 0.0031495 | 3.4636 | 8.2622e-05 | 0.043815 | 4.686 | 0 | 4.7298 |  | 15.1298 | 4 | 15.1298 | 69.5613 | 34.7807 | 15 | 35 | -0.21933 | -10.101 | 0.0031495 | -5.1639e-05 | -1 | 0
535 | 8.9167 | 4.998 | 11.9968 | 5 | 12 | 69.5953 | 40 | 0.0032267 | 3.4668 | 7.7138e-05 | 0.044888 | 4.6904 | 0 | 4.7353 |  | 15.1353 | 4 | 15.1353 | 69.5953 | 34.7977 | 15 | 35 | -0.20233 | -10.3033 | 0.0032267 | -4.8211e-05 | -1 | 0
536 | 8.9333 | 4.9979 | 11.9967 | 5 | 12 | 69.6295 | 40 | 0.0032983 | 3.4701 | 7.1617e-05 | 0.045884 | 4.6948 | 0 | 4.7407 |  | 15.1407 | 4 | 15.1407 | 69.6295 | 34.8147 | 15 | 35 | -0.18527 | -10.4886 | 0.0032983 | -4.4761e-05 | -1 | 0
537 | 8.95 | 4.9979 | 11.9966 | 5 | 12 | 69.6636 | 40 | 0.0033644 | 3.4735 | 6.6067e-05 | 0.046803 | 4.6994 | 0 | 4.7462 |  | 15.1462 | 4 | 15.1462 | 69.6636 | 34.8318 | 15 | 35 | -0.16818 | -10.6568 | 0.0033644 | -4.1292e-05 | -1 | 0
538 | 8.9667 | 4.9979 | 11.9966 | 5 | 12 | 69.6979 | 40 | 0.0034249 | 3.4769 | 6.0497e-05 | 0.047645 | 4.704 | 0 | 4.7517 |  | 15.1517 | 4 | 15.1517 | 69.6979 | 34.8489 | 15 | 35 | -0.15107 | -10.8078 | 0.0034249 | -3.7811e-05 | -1 | 0
539 | 8.9833 | 4.9978 | 11.9965 | 5 | 12 | 69.7321 | 40 | 0.0034798 | 3.4804 | 5.4915e-05 | 0.048409 | 4.7087 | 0 | 4.7571 |  | 15.1571 | 4 | 15.1571 | 69.7321 | 34.866 | 15 | 35 | -0.13397 | -10.9418 | 0.0034798 | -3.4322e-05 | -1 | 0
540 | 9 | 4.9978 | 11.9965 | 5 | 12 | 69.7662 | 40 | 0.0035291 | 3.4839 | 4.9328e-05 | 0.049095 | 4.7135 | 0 | 4.7626 |  | 15.1626 | 4 | 15.1626 | 69.7662 | 34.8831 | 15 | 35 | -0.1169 | -11.0587 | 0.0035291 | -3.083e-05 | -1 | 0
541 | 9.0167 | 4.9978 | 11.9964 | 5 | 12 | 69.8002 | 40 | 0.0035728 | 3.4875 | 4.3744e-05 | 0.049704 | 4.7183 | 0 | 4.768 |  | 15.168 | 4 | 15.168 | 69.8002 | 34.9001 | 15 | 35 | -0.099894 | -11.1586 | 0.0035728 | -2.734e-05 | -1 | 0
542 | 9.0333 | 4.9977 | 11.9964 | 5 | 12 | 69.8341 | 40 | 0.003611 | 3.4911 | 3.8172e-05 | 0.050235 | 4.7232 | 0 | 4.7735 |  | 15.1735 | 4 | 15.1735 | 69.8341 | 34.917 | 15 | 35 | -0.082967 | -11.2416 | 0.003611 | -2.3857e-05 | -1 | 0
543 | 9.05 | 4.9977 | 11.9964 | 5 | 12 | 69.8677 | 40 | 0.0036436 | 3.4947 | 3.2618e-05 | 0.050689 | 4.7281 | 0 | 4.7788 |  | 15.1788 | 4 | 15.1788 | 69.8677 | 34.9339 | 15 | 35 | -0.066144 | -11.3077 | 0.0036436 | -2.0386e-05 | -1 | 0
544 | 9.0667 | 4.9977 | 11.9963 | 5 | 12 | 69.9011 | 40 | 0.0036707 | 3.4984 | 2.7091e-05 | 0.051065 | 4.7331 | 0 | 4.7842 |  | 15.1842 | 4 | 15.1842 | 69.9011 | 34.9506 | 15 | 35 | -0.049447 | -11.3572 | 0.0036707 | -1.6932e-05 | -1 | 0
545 | 9.0833 | 4.9977 | 11.9963 | 5 | 12 | 69.9342 | 40 | 0.0036923 | 3.5021 | 2.1598e-05 | 0.051366 | 4.7381 | 0 | 4.7895 |  | 15.1895 | 4 | 15.1895 | 69.9342 | 34.9671 | 15 | 35 | -0.032897 | -11.3901 | 0.0036923 | -1.3499e-05 | -1 | 0
546 | 9.1 | 4.9977 | 11.9963 | 5 | 12 | 69.967 | 40 | 0.0037085 | 3.5058 | 1.6146e-05 | 0.05159 | 4.7431 | 0 | 4.7947 |  | 15.1947 | 4 | 15.1947 | 69.967 | 34.9835 | 15 | 35 | -0.016516 | -11.4066 | 0.0037085 | -1.0091e-05 | -1 | 0
547 | 9.1167 | 4.9977 | 11.9963 | 5 | 12 | 69.9994 | 40 | 0.0037192 | 3.5095 | 1.0742e-05 | 0.05174 | 4.7482 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9994 | 34.9997 | 15 | 35 | -0.00032417 | -11.4069 | 0.0037192 | -6.7136e-06 | -1 | 0
548 | 9.1333 | 4.9977 | 11.9963 | 5 | 12 | 70.0313 | 40 | 0.0037246 | 3.5132 | 5.3929e-06 | 0.051815 | 4.7532 | 0 | 4.805 |  | 15.205 | 4 | 15.205 | 70.0313 | 35.0157 | 15 | 35 | 0.015658 | -11.3912 | 0.0037246 | -3.3706e-06 | -1 | 0
549 | 9.15 | 4.9977 | 11.9963 | 5 | 12 | 70.0628 | 40 | 0.0037247 | 3.517 | 1.0585e-07 | 0.051816 | 4.7582 | 0 | 4.8101 |  | 15.2101 | 4 | 15.2101 | 70.0628 | 35.0314 | 15 | 35 | 0.03141 | -11.3598 | 0.0037247 | -6.6158e-08 | -1 | 0
550 | 9.1667 | 4.9977 | 11.9963 | 5 | 12 | 70.0938 | 40 | 0.0037196 | 3.5207 | -5.1127e-06 | 0.051745 | 4.7633 | 0 | 4.815 |  | 15.215 | 4 | 15.215 | 70.0938 | 35.0469 | 15 | 35 | 0.046914 | -11.3129 | 0.0037196 | 3.1954e-06 | 1 | 2
551 | 9.1833 | 4.9977 | 11.9963 | 5 | 12 | 70.1243 | 40 | 0.0037093 | 3.5244 | -1.0256e-05 | 0.051603 | 4.7683 | 0 | 4.8199 |  | 15.2199 | 4 | 15.2199 | 70.1243 | 35.0622 | 15 | 35 | 0.062151 | -11.2508 | 0.0037093 | 6.4102e-06 | 1 | 0
552 | 9.2 | 4.9977 | 11.9963 | 5 | 12 | 70.1542 | 40 | 0.003694 | 3.5281 | -1.5319e-05 | 0.051389 | 4.7733 | 0 | 4.8247 |  | 15.2247 | 4 | 15.2247 | 70.1542 | 35.0771 | 15 | 35 | 0.077103 | -11.1737 | 0.003694 | 9.5743e-06 | 1 | 0
553 | 9.2167 | 4.9977 | 11.9963 | 5 | 12 | 70.1835 | 40 | 0.0036737 | 3.5318 | -2.0294e-05 | 0.051107 | 4.7783 | 0 | 4.8294 |  | 15.2294 | 4 | 15.2294 | 70.1835 | 35.0918 | 15 | 35 | 0.091753 | -11.0819 | 0.0036737 | 1.2684e-05 | 1 | 0
554 | 9.2333 | 4.9977 | 11.9964 | 5 | 12 | 70.2122 | 40 | 0.0036485 | 3.5354 | -2.5177e-05 | 0.050757 | 4.7832 | 0 | 4.8339 |  | 15.2339 | 4 | 15.2339 | 70.2122 | 35.1061 | 15 | 35 | 0.10608 | -10.9758 | 0.0036485 | 1.5735e-05 | 1 | 0
555 | 9.25 | 4.9977 | 11.9964 | 5 | 12 | 70.2402 | 40 | 0.0036186 | 3.539 | -2.996e-05 | 0.05034 | 4.7881 | 0 | 4.8384 |  | 15.2384 | 4 | 15.2384 | 70.2402 | 35.1201 | 15 | 35 | 0.12008 | -10.8557 | 0.0036186 | 1.8725e-05 | 1 | 0
556 | 9.2667 | 4.9978 | 11.9964 | 5 | 12 | 70.2675 | 40 | 0.0035839 | 3.5426 | -3.464e-05 | 0.049858 | 4.7929 | 0 | 4.8428 |  | 15.2428 | 4 | 15.2428 | 70.2675 | 35.1337 | 15 | 35 | 0.13373 | -10.722 | 0.0035839 | 2.165e-05 | 1 | 0
557 | 9.2833 | 4.9978 | 11.9965 | 5 | 12 | 70.294 | 40 | 0.0035447 | 3.5461 | -3.921e-05 | 0.049313 | 4.7977 | 0 | 4.847 |  | 15.247 | 4 | 15.247 | 70.294 | 35.147 | 15 | 35 | 0.14701 | -10.575 | 0.0035447 | 2.4506e-05 | 1 | 0
558 | 9.3 | 4.9978 | 11.9965 | 5 | 12 | 70.3198 | 40 | 0.0035011 | 3.5496 | -4.3666e-05 | 0.048705 | 4.8025 | 0 | 4.8512 |  | 15.2512 | 4 | 15.2512 | 70.3198 | 35.1599 | 15 | 35 | 0.15991 | -10.4151 | 0.0035011 | 2.7291e-05 | 1 | 0
559 | 9.3167 | 4.9978 | 11.9965 | 5 | 12 | 70.3449 | 40 | 0.0034531 | 3.5531 | -4.8003e-05 | 0.048037 | 4.8071 | 0 | 4.8552 |  | 15.2552 | 4 | 15.2552 | 70.3449 | 35.1724 | 15 | 35 | 0.17243 | -10.2427 | 0.0034531 | 3.0002e-05 | 1 | 0
560 | 9.3333 | 4.9979 | 11.9966 | 5 | 12 | 70.3691 | 40 | 0.0034008 | 3.5565 | -5.2217e-05 | 0.047311 | 4.8117 | 0 | 4.8591 |  | 15.2591 | 4 | 15.2591 | 70.3691 | 35.1845 | 15 | 35 | 0.18454 | -10.0581 | 0.0034008 | 3.2636e-05 | 1 | 0
561 | 9.35 | 4.9979 | 11.9967 | 5 | 12 | 70.3925 | 40 | 0.0033445 | 3.5598 | -5.6303e-05 | 0.046528 | 4.8163 | 0 | 4.8628 |  | 15.2628 | 4 | 15.2628 | 70.3925 | 35.1962 | 15 | 35 | 0.19623 | -9.8619 | 0.0033445 | 3.5189e-05 | 1 | 0
562 | 9.3667 | 4.9979 | 11.9967 | 5 | 12 | 70.415 | 40 | 0.0032843 | 3.5631 | -6.0256e-05 | 0.04569 | 4.8207 | 0 | 4.8664 |  | 15.2664 | 4 | 15.2664 | 70.415 | 35.2075 | 15 | 35 | 0.20749 | -9.6544 | 0.0032843 | 3.766e-05 | 1 | 0
563 | 9.3833 | 4.998 | 11.9968 | 5 | 12 | 70.4366 | 40 | 0.0032202 | 3.5664 | -6.4074e-05 | 0.044798 | 4.8251 | 0 | 4.8699 |  | 15.2699 | 4 | 15.2699 | 70.4366 | 35.2183 | 15 | 35 | 0.21832 | -9.4361 | 0.0032202 | 4.0047e-05 | 1 | 0
564 | 9.4 | 4.998 | 11.9968 | 5 | 12 | 70.4574 | 40 | 0.0031525 | 3.5695 | -6.7753e-05 | 0.043856 | 4.8293 | 0 | 4.8732 |  | 15.2732 | 4 | 15.2732 | 70.4574 | 35.2287 | 15 | 35 | 0.22871 | -9.2074 | 0.0031525 | 4.2346e-05 | 1 | 0
565 | 9.4167 | 4.9981 | 11.9969 | 5 | 12 | 70.4773 | 40 | 0.0030812 | 3.5726 | -7.1289e-05 | 0.042864 | 4.8335 | 0 | 4.8764 |  | 15.2764 | 4 | 15.2764 | 70.4773 | 35.2386 | 15 | 35 | 0.23863 | -8.9687 | 0.0030812 | 4.4556e-05 | 1 | 0
566 | 9.4333 | 4.9981 | 11.997 | 5 | 12 | 70.4962 | 40 | 0.0030065 | 3.5756 | -7.468e-05 | 0.041825 | 4.8376 | 0 | 4.8794 |  | 15.2794 | 4 | 15.2794 | 70.4962 | 35.2481 | 15 | 35 | 0.2481 | -8.7206 | 0.0030065 | 4.6675e-05 | 1 | 0
567 | 9.45 | 4.9982 | 11.9971 | 5 | 12 | 70.5142 | 40 | 0.0029286 | 3.5785 | -7.7921e-05 | 0.040741 | 4.8415 | 0 | 4.8823 |  | 15.2823 | 4 | 15.2823 | 70.5142 | 35.2571 | 15 | 35 | 0.25709 | -8.4636 | 0.0029286 | 4.8701e-05 | 1 | 0
568 | 9.4667 | 4.9982 | 11.9972 | 5 | 12 | 70.5312 | 40 | 0.0028476 | 3.5814 | -8.1012e-05 | 0.039614 | 4.8454 | 0 | 4.885 |  | 15.285 | 4 | 15.285 | 70.5312 | 35.2656 | 15 | 35 | 0.26561 | -8.1979 | 0.0028476 | 5.0632e-05 | 1 | 0
569 | 9.4833 | 4.9983 | 11.9972 | 5 | 12 | 70.5473 | 40 | 0.0027636 | 3.5841 | -8.3949e-05 | 0.038446 | 4.8491 | 0 | 4.8876 |  | 15.2876 | 4 | 15.2876 | 70.5473 | 35.2736 | 15 | 35 | 0.27365 | -7.9243 | 0.0027636 | 5.2468e-05 | 1 | 0
570 | 9.5 | 4.9983 | 11.9973 | 5 | 12 | 70.5624 | 40 | 0.0026769 | 3.5868 | -8.673e-05 | 0.03724 | 4.8527 | 0 | 4.89 |  | 15.29 | 4 | 15.29 | 70.5624 | 35.2812 | 15 | 35 | 0.28119 | -7.6431 | 0.0026769 | 5.4206e-05 | 1 | 0
571 | 9.5167 | 4.9984 | 11.9974 | 5 | 12 | 70.5765 | 40 | 0.0025875 | 3.5894 | -8.9354e-05 | 0.035997 | 4.8562 | 0 | 4.8922 |  | 15.2922 | 4 | 15.2922 | 70.5765 | 35.2882 | 15 | 35 | 0.28825 | -7.3549 | 0.0025875 | 5.5846e-05 | 1 | 0
572 | 9.5333 | 4.9984 | 11.9975 | 5 | 12 | 70.5896 | 40 | 0.0024957 | 3.5919 | -9.1818e-05 | 0.034719 | 4.8596 | 0 | 4.8943 |  | 15.2943 | 4 | 15.2943 | 70.5896 | 35.2948 | 15 | 35 | 0.29481 | -7.06 | 0.0024957 | 5.7386e-05 | 1 | 0
573 | 9.55 | 4.9985 | 11.9976 | 5 | 12 | 70.6017 | 40 | 0.0024016 | 3.5943 | -9.4122e-05 | 0.03341 | 4.8629 | 0 | 4.8963 |  | 15.2963 | 4 | 15.2963 | 70.6017 | 35.3009 | 15 | 35 | 0.30087 | -6.7592 | 0.0024016 | 5.8826e-05 | 1 | 0
574 | 9.5667 | 4.9986 | 11.9977 | 5 | 12 | 70.6129 | 40 | 0.0023053 | 3.5966 | -9.6264e-05 | 0.032071 | 4.866 | 0 | 4.8981 |  | 15.2981 | 4 | 15.2981 | 70.6129 | 35.3064 | 15 | 35 | 0.30643 | -6.4527 | 0.0023053 | 6.0165e-05 | 1 | 0
575 | 9.5833 | 4.9986 | 11.9978 | 5 | 12 | 70.623 | 40 | 0.0022071 | 3.5988 | -9.8243e-05 | 0.030704 | 4.869 | 0 | 4.8997 |  | 15.2997 | 4 | 15.2997 | 70.623 | 35.3115 | 15 | 35 | 0.31149 | -6.1413 | 0.0022071 | 6.1402e-05 | 1 | 0
576 | 9.6 | 4.9987 | 11.9979 | 5 | 12 | 70.6321 | 40 | 0.002107 | 3.6009 | -0.00010006 | 0.029312 | 4.8718 | 0 | 4.9011 |  | 15.3011 | 4 | 15.3011 | 70.6321 | 35.3161 | 15 | 35 | 0.31605 | -5.8252 | 0.002107 | 6.2537e-05 | 1 | 0
577 | 9.6167 | 4.9987 | 11.998 | 5 | 12 | 70.6402 | 40 | 0.0020053 | 3.6029 | -0.00010171 | 0.027897 | 4.8745 | 0 | 4.9024 |  | 15.3024 | 4 | 15.3024 | 70.6402 | 35.3201 | 15 | 35 | 0.32011 | -5.5051 | 0.0020053 | 6.357e-05 | 1 | 0
578 | 9.6333 | 4.9988 | 11.9981 | 5 | 12 | 70.6473 | 40 | 0.0019021 | 3.6048 | -0.0001032 | 0.026461 | 4.8771 | 0 | 4.9036 |  | 15.3036 | 4 | 15.3036 | 70.6473 | 35.3237 | 15 | 35 | 0.32366 | -5.1814 | 0.0019021 | 6.45e-05 | 1 | 0
579 | 9.65 | 4.9989 | 11.9982 | 5 | 12 | 70.6534 | 40 | 0.0017976 | 3.6066 | -0.00010452 | 0.025007 | 4.8795 | 0 | 4.9046 |  | 15.3046 | 4 | 15.3046 | 70.6534 | 35.3267 | 15 | 35 | 0.32672 | -4.8547 | 0.0017976 | 6.5328e-05 | 1 | 0
580 | 9.6667 | 4.9989 | 11.9983 | 5 | 12 | 70.6586 | 40 | 0.0016919 | 3.6083 | -0.00010569 | 0.023537 | 4.8818 | 0 | 4.9054 |  | 15.3054 | 4 | 15.3054 | 70.6586 | 35.3293 | 15 | 35 | 0.32928 | -4.5254 | 0.0016919 | 6.6054e-05 | 1 | 0
581 | 9.6833 | 4.999 | 11.9984 | 5 | 12 | 70.6627 | 40 | 0.0015852 | 3.6099 | -0.00010668 | 0.022053 | 4.884 | 0 | 4.906 |  | 15.306 | 4 | 15.306 | 70.6627 | 35.3313 | 15 | 35 | 0.33134 | -4.1941 | 0.0015852 | 6.6677e-05 | 1 | 0
582 | 9.7 | 4.9991 | 11.9985 | 5 | 12 | 70.6658 | 40 | 0.0014777 | 3.6114 | -0.00010752 | 0.020557 | 4.886 | 0 | 4.9065 |  | 15.3065 | 4 | 15.3065 | 70.6658 | 35.3329 | 15 | 35 | 0.33292 | -3.8612 | 0.0014777 | 6.7199e-05 | 1 | 0
583 | 9.7167 | 4.9991 | 11.9986 | 5 | 12 | 70.668 | 40 | 0.0013695 | 3.6127 | -0.00010819 | 0.019052 | 4.8878 | 0 | 4.9069 |  | 15.3069 | 4 | 15.3069 | 70.668 | 35.334 | 15 | 35 | 0.334 | -3.5272 | 0.0013695 | 6.7621e-05 | 1 | 0
584 | 9.7333 | 4.9992 | 11.9987 | 5 | 12 | 70.6692 | 40 | 0.0012608 | 3.614 | -0.00010871 | 0.01754 | 4.8895 | 0 | 4.9071 |  | 15.3071 | 4 | 15.3071 | 70.6692 | 35.3346 | 15 | 35 | 0.33461 | -3.1926 | 0.0012608 | 6.7942e-05 | 1 | 0
585 | 9.75 | 4.9993 | 11.9988 | 5 | 12 | 70.6695 | 40 | 0.0011517 | 3.6152 | -0.00010906 | 0.016022 | 4.8911 | 0 | 4.9071 |  | 15.3071 | 4 | 15.3071 | 70.6695 | 35.3347 | 15 | 35 | 0.33473 | -2.8578 | 0.0011517 | 6.8164e-05 | 1 | 0
586 | 9.7667 | 4.9993 | 11.999 | 5 | 12 | 70.6688 | 40 | 0.0010425 | 3.6162 | -0.00010926 | 0.014502 | 4.8925 | 0 | 4.907 |  | 15.307 | 4 | 15.307 | 70.6688 | 35.3344 | 15 | 35 | 0.33439 | -2.5234 | 0.0010425 | 6.8287e-05 | 1 | 0
587 | 9.7833 | 4.9994 | 11.9991 | 5 | 12 | 70.6672 | 40 | 0.00093317 | 3.6171 | -0.0001093 | 0.012982 | 4.8938 | 0 | 4.9067 |  | 15.3067 | 4 | 15.3067 | 70.6672 | 35.3336 | 15 | 35 | 0.33359 | -2.1899 | 0.00093317 | 6.8313e-05 | 1 | 0
588 | 9.8 | 4.9995 | 11.9992 | 5 | 12 | 70.6646 | 40 | 0.00082398 | 3.618 | -0.00010919 | 0.011463 | 4.8949 | 0 | 4.9063 |  | 15.3063 | 4 | 15.3063 | 70.6646 | 35.3323 | 15 | 35 | 0.33232 | -1.8575 | 0.00082398 | 6.8243e-05 | 1 | 0
589 | 9.8167 | 4.9996 | 11.9993 | 5 | 12 | 70.6612 | 40 | 0.00071506 | 3.6187 | -0.00010893 | 0.0099475 | 4.8958 | 0 | 4.9058 |  | 15.3058 | 4 | 15.3058 | 70.6612 | 35.3306 | 15 | 35 | 0.33061 | -1.5269 | 0.00071506 | 6.8079e-05 | 1 | 0
590 | 9.8333 | 4.9996 | 11.9994 | 5 | 12 | 70.6569 | 40 | 0.00060654 | 3.6193 | -0.00010851 | 0.0084379 | 4.8967 | 0 | 4.9051 |  | 15.3051 | 4 | 15.3051 | 70.6569 | 35.3285 | 15 | 35 | 0.32846 | -1.1985 | 0.00060654 | 6.7821e-05 | 1 | 0
591 | 9.85 | 4.9997 | 11.9995 | 5 | 12 | 70.6517 | 40 | 0.00049859 | 3.6198 | -0.00010795 | 0.0069361 | 4.8973 | 0 | 4.9043 |  | 15.3043 | 4 | 15.3043 | 70.6517 | 35.3259 | 15 | 35 | 0.32587 | -0.8726 | 0.00049859 | 6.7472e-05 | 1 | 0
592 | 9.8667 | 4.9998 | 11.9996 | 5 | 12 | 70.6457 | 40 | 0.00039134 | 3.6202 | -0.00010725 | 0.0054441 | 4.8979 | 0 | 4.9033 |  | 15.3033 | 4 | 15.3033 | 70.6457 | 35.3229 | 15 | 35 | 0.32286 | -0.54973 | 0.00039134 | 6.7032e-05 | 1 | 0
593 | 9.8833 | 4.9998 | 11.9997 | 5 | 12 | 70.6389 | 40 | 0.00028493 | 3.6205 | -0.00010641 | 0.0039638 | 4.8983 | 0 | 4.9022 |  | 15.3022 | 4 | 15.3022 | 70.6389 | 35.3194 | 15 | 35 | 0.31944 | -0.23029 | 0.00028493 | 6.6505e-05 | 1 | 0
594 | 9.9 | 4.9999 | 11.9998 | 5 | 12 | 70.6312 | 40 | 0.0001795 | 3.6206 | -0.00010543 | 0.0024972 | 4.8985 | 0 | 4.901 |  | 15.301 | 4 | 15.301 | 70.6312 | 35.3156 | 15 | 35 | 0.31562 | 0.08533 | 0.0001795 | 6.5891e-05 | 1 | 0
595 | 9.9167 | 5 | 11.9999 | 5 | 12 | 70.6228 | 40 | 7.5196e-05 | 3.6207 | -0.00010431 | 0.0010461 | 4.8986 | 0 | 4.8996 |  | 15.2996 | 4 | 15.2996 | 70.6228 | 35.3114 | 15 | 35 | 0.3114 | 0.39673 | 7.5196e-05 | 6.5192e-05 | 1 | 0
596 | 9.9333 | 5 | 12 | 5 | 12 | 70.6136 | 40 | -2.7863e-05 | 3.6207 | -0.00010306 | -0.00038762 | 4.8986 | 0 | 4.8982 |  | 15.2982 | 4 | 15.2982 | 70.6136 | 35.3068 | 15 | 35 | 0.3068 | 0.70354 | 2.7863e-05 | 6.4412e-05 | 1 | 0
597 | 9.95 | 5.0001 | 12.0001 | 5 | 12 | 70.6037 | 40 | -0.00012955 | 3.6205 | -0.00010168 | -0.0018022 | 4.8984 | 0 | 4.8966 |  | 15.2966 | 4 | 15.2966 | 70.6037 | 35.3018 | 15 | 35 | 0.30184 | 1.0054 | 0.00012955 | 6.3551e-05 | 1 | 0
598 | 9.9667 | 5.0001 | 12.0002 | 5 | 12 | 70.593 | 40 | -0.00022973 | 3.6203 | -0.00010018 | -0.0031958 | 4.8981 | 0 | 4.8949 |  | 15.2949 | 4 | 15.2949 | 70.593 | 35.2965 | 15 | 35 | 0.29651 | 1.3019 | 0.00022973 | 6.2613e-05 | 1 | 0
599 | 9.9833 | 5.0002 | 12.0003 | 5 | 12 | 70.5817 | 40 | -0.00032828 | 3.62 | -9.8559e-05 | -0.004567 | 4.8976 | 0 | 4.8931 |  | 15.2931 | 4 | 15.2931 | 70.5817 | 35.2908 | 15 | 35 | 0.29084 | 1.5927 | 0.00032828 | 6.1599e-05 | 1 | 0
600 | 10 | 5.0003 | 12.0004 | 5 | 12 | 70.5697 | 40 | -0.0004251 | 3.6196 | -9.6819e-05 | -0.0059139 | 4.8971 | 0 | 4.8911 |  | 15.2911 | 4 | 15.2911 | 70.5697 | 35.2848 | 15 | 35 | 0.28483 | 1.8775 | 0.0004251 | 6.0512e-05 | 1 | 0
601 | 10.0167 | 5.0003 | 12.0005 | 5 | 12 | 70.557 | 40 | -0.00052007 | 3.619 | -9.4967e-05 | -0.007235 | 4.8964 | 0 | 4.8891 |  | 15.2891 | 4 | 15.2891 | 70.557 | 35.2785 | 15 | 35 | 0.2785 | 2.1561 | 0.00052007 | 5.9354e-05 | 1 | 0
602 | 10.0333 | 5.0004 | 12.0006 | 5 | 12 | 70.5437 | 40 | -0.00061308 | 3.6184 | -9.3006e-05 | -0.0085289 | 4.8955 | 0 | 4.887 |  | 15.287 | 4 | 15.287 | 70.5437 | 35.2719 | 15 | 35 | 0.27187 | 2.4279 | 0.00061308 | 5.8129e-05 | 1 | 0
603 | 10.05 | 5.0004 | 12.0007 | 5 | 12 | 70.5299 | 40 | -0.00070402 | 3.6177 | -9.094e-05 | -0.009794 | 4.8946 | 0 | 4.8848 |  | 15.2848 | 4 | 15.2848 | 70.5299 | 35.2649 | 15 | 35 | 0.26494 | 2.6929 | 0.00070402 | 5.6837e-05 | 1 | 0
604 | 10.0667 | 5.0005 | 12.0008 | 5 | 12 | 70.5155 | 40 | -0.00079279 | 3.6169 | -8.8773e-05 | -0.011029 | 4.8935 | 0 | 4.8825 |  | 15.2825 | 4 | 15.2825 | 70.5155 | 35.2577 | 15 | 35 | 0.25773 | 2.9506 | 0.00079279 | 5.5483e-05 | 1 | 0
605 | 10.0833 | 5.0005 | 12.0009 | 5 | 12 | 70.5005 | 40 | -0.0008793 | 3.6161 | -8.651e-05 | -0.012232 | 4.8923 | 0 | 4.8801 |  | 15.2801 | 4 | 15.2801 | 70.5005 | 35.2502 | 15 | 35 | 0.25025 | 3.2008 | 0.0008793 | 5.4069e-05 | 1 | 0
606 | 10.1 | 5.0006 | 12.001 | 5 | 12 | 70.485 | 40 | -0.00096346 | 3.6151 | -8.4155e-05 | -0.013403 | 4.891 | 0 | 4.8776 |  | 15.2776 | 4 | 15.2776 | 70.485 | 35.2425 | 15 | 35 | 0.24252 | 3.4433 | 0.00096346 | 5.2597e-05 | 1 | 0
607 | 10.1167 | 5.0007 | 12.001 | 5 | 12 | 70.4691 | 40 | -0.0010452 | 3.614 | -8.1714e-05 | -0.01454 | 4.8896 | 0 | 4.8751 |  | 15.2751 | 4 | 15.2751 | 70.4691 | 35.2345 | 15 | 35 | 0.23454 | 3.6779 | 0.0010452 | 5.1071e-05 | 1 | 0
608 | 10.1333 | 5.0007 | 12.0011 | 5 | 12 | 70.4527 | 40 | -0.0011244 | 3.6129 | -7.9189e-05 | -0.015642 | 4.8881 | 0 | 4.8724 |  | 15.2724 | 4 | 15.2724 | 70.4527 | 35.2263 | 15 | 35 | 0.22635 | 3.9042 | 0.0011244 | 4.9493e-05 | 1 | 0
609 | 10.15 | 5.0008 | 12.0012 | 5 | 12 | 70.4359 | 40 | -0.0012009 | 3.6117 | -7.6586e-05 | -0.016707 | 4.8864 | 0 | 4.8697 |  | 15.2697 | 4 | 15.2697 | 70.4359 | 35.2179 | 15 | 35 | 0.21794 | 4.1222 | 0.0012009 | 4.7866e-05 | 1 | 0
610 | 10.1667 | 5.0008 | 12.0013 | 5 | 12 | 70.4187 | 40 | -0.0012749 | 3.6104 | -7.391e-05 | -0.017735 | 4.8847 | 0 | 4.867 |  | 15.267 | 4 | 15.267 | 70.4187 | 35.2093 | 15 | 35 | 0.20934 | 4.3315 | 0.0012749 | 4.6193e-05 | 1 | 0
611 | 10.1833 | 5.0008 | 12.0013 | 5 | 12 | 70.4011 | 40 | -0.001346 | 3.6091 | -7.1164e-05 | -0.018725 | 4.8829 | 0 | 4.8642 |  | 15.2642 | 4 | 15.2642 | 70.4011 | 35.2006 | 15 | 35 | 0.20055 | 4.5321 | 0.001346 | 4.4478e-05 | 1 | 0
612 | 10.2 | 5.0009 | 12.0014 | 5 | 12 | 70.3832 | 40 | -0.0014144 | 3.6077 | -6.8355e-05 | -0.019676 | 4.881 | 0 | 4.8613 |  | 15.2613 | 4 | 15.2613 | 70.3832 | 35.1916 | 15 | 35 | 0.1916 | 4.7237 | 0.0014144 | 4.2722e-05 | 1 | 0
613 | 10.2167 | 5.0009 | 12.0015 | 5 | 12 | 70.365 | 40 | -0.0014799 | 3.6062 | -6.5487e-05 | -0.020587 | 4.879 | 0 | 4.8584 |  | 15.2584 | 4 | 15.2584 | 70.365 | 35.1825 | 15 | 35 | 0.1825 | 4.9062 | 0.0014799 | 4.0929e-05 | 1 | 0
614 | 10.2333 | 5.001 | 12.0015 | 5 | 12 | 70.3465 | 40 | -0.0015424 | 3.6047 | -6.2564e-05 | -0.021458 | 4.8769 | 0 | 4.8554 |  | 15.2554 | 4 | 15.2554 | 70.3465 | 35.1733 | 15 | 35 | 0.17326 | 5.0794 | 0.0015424 | 3.9102e-05 | 1 | 0
615 | 10.25 | 5.001 | 12.0016 | 5 | 12 | 70.3278 | 40 | -0.001602 | 3.6031 | -5.9591e-05 | -0.022287 | 4.8747 | 0 | 4.8524 |  | 15.2524 | 4 | 15.2524 | 70.3278 | 35.1639 | 15 | 35 | 0.16389 | 5.2433 | 0.001602 | 3.7245e-05 | 1 | 0
616 | 10.2667 | 5.001 | 12.0017 | 5 | 12 | 70.3088 | 40 | -0.0016586 | 3.6014 | -5.6574e-05 | -0.023074 | 4.8725 | 0 | 4.8494 |  | 15.2494 | 4 | 15.2494 | 70.3088 | 35.1544 | 15 | 35 | 0.15442 | 5.3977 | 0.0016586 | 3.5359e-05 | 1 | 0
617 | 10.2833 | 5.0011 | 12.0017 | 5 | 12 | 70.2897 | 40 | -0.0017121 | 3.5997 | -5.3516e-05 | -0.023818 | 4.8702 | 0 | 4.8464 |  | 15.2464 | 4 | 15.2464 | 70.2897 | 35.1449 | 15 | 35 | 0.14486 | 5.5426 | 0.0017121 | 3.3448e-05 | 1 | 0
618 | 10.3 | 5.0011 | 12.0018 | 5 | 12 | 70.2704 | 40 | -0.0017625 | 3.5979 | -5.0423e-05 | -0.02452 | 4.8678 | 0 | 4.8433 |  | 15.2433 | 4 | 15.2433 | 70.2704 | 35.1352 | 15 | 35 | 0.13521 | 5.6778 | 0.0017625 | 3.1515e-05 | 1 | 0
619 | 10.3167 | 5.0011 | 12.0018 | 5 | 12 | 70.251 | 40 | -0.0018098 | 3.5961 | -4.73e-05 | -0.025178 | 4.8653 | 0 | 4.8402 |  | 15.2402 | 4 | 15.2402 | 70.251 | 35.1255 | 15 | 35 | 0.1255 | 5.8033 | 0.0018098 | 2.9562e-05 | 1 | 0
620 | 10.3333 | 5.0012 | 12.0019 | 5 | 12 | 70.2315 | 40 | -0.001854 | 3.5943 | -4.4151e-05 | -0.025792 | 4.8628 | 0 | 4.837 |  | 15.237 | 4 | 15.237 | 70.2315 | 35.1157 | 15 | 35 | 0.11575 | 5.9191 | 0.001854 | 2.7594e-05 | 1 | 0
621 | 10.35 | 5.0012 | 12.0019 | 5 | 12 | 70.2119 | 40 | -0.001895 | 3.5924 | -4.0981e-05 | -0.026362 | 4.8603 | 0 | 4.8339 |  | 15.2339 | 4 | 15.2339 | 70.2119 | 35.106 | 15 | 35 | 0.10595 | 6.025 | 0.001895 | 2.5613e-05 | 1 | 0
622 | 10.3667 | 5.0012 | 12.0019 | 5 | 12 | 70.1923 | 40 | -0.0019328 | 3.5904 | -3.7795e-05 | -0.026888 | 4.8577 | 0 | 4.8308 |  | 15.2308 | 4 | 15.2308 | 70.1923 | 35.0961 | 15 | 35 | 0.096138 | 6.1211 | 0.0019328 | 2.3622e-05 | 1 | 0
623 | 10.3833 | 5.0012 | 12.002 | 5 | 12 | 70.1726 | 40 | -0.0019674 | 3.5885 | -3.4597e-05 | -0.027369 | 4.855 | 0 | 4.8276 |  | 15.2276 | 4 | 15.2276 | 70.1726 | 35.0863 | 15 | 35 | 0.086316 | 6.2075 | 0.0019674 | 2.1623e-05 | 1 | 0
624 | 10.4 | 5.0012 | 12.002 | 5 | 12 | 70.153 | 40 | -0.0019987 | 3.5865 | -3.1392e-05 | -0.027806 | 4.8523 | 0 | 4.8245 |  | 15.2245 | 4 | 15.2245 | 70.153 | 35.0765 | 15 | 35 | 0.076501 | 6.284 | 0.0019987 | 1.962e-05 | 1 | 0
625 | 10.4167 | 5.0013 | 12.002 | 5 | 12 | 70.1334 | 40 | -0.0020269 | 3.5844 | -2.8185e-05 | -0.028198 | 4.8495 | 0 | 4.8213 |  | 15.2213 | 4 | 15.2213 | 70.1334 | 35.0667 | 15 | 35 | 0.066706 | 6.3507 | 0.0020269 | 1.7616e-05 | 1 | 0
626 | 10.4333 | 5.0013 | 12.0021 | 5 | 12 | 70.1139 | 40 | -0.0020519 | 3.5824 | -2.498e-05 | -0.028545 | 4.8468 | 0 | 4.8182 |  | 15.2182 | 4 | 15.2182 | 70.1139 | 35.0569 | 15 | 35 | 0.056944 | 6.4076 | 0.0020519 | 1.5612e-05 | 1 | 0
627 | 10.45 | 5.0013 | 12.0021 | 5 | 12 | 70.0945 | 40 | -0.0020737 | 3.5803 | -2.1781e-05 | -0.028848 | 4.844 | 0 | 4.8151 |  | 15.2151 | 4 | 15.2151 | 70.0945 | 35.0472 | 15 | 35 | 0.04723 | 6.4548 | 0.0020737 | 1.3613e-05 | 1 | 0
628 | 10.4667 | 5.0013 | 12.0021 | 5 | 12 | 70.0752 | 40 | -0.0020923 | 3.5782 | -1.8594e-05 | -0.029107 | 4.8411 | 0 | 4.812 |  | 15.212 | 4 | 15.212 | 70.0752 | 35.0376 | 15 | 35 | 0.037576 | 6.4924 | 0.0020923 | 1.1621e-05 | 1 | 0
629 | 10.4833 | 5.0013 | 12.0021 | 5 | 12 | 70.056 | 40 | -0.0021077 | 3.5761 | -1.5422e-05 | -0.029321 | 4.8383 | 0 | 4.809 |  | 15.209 | 4 | 15.209 | 70.056 | 35.028 | 15 | 35 | 0.027994 | 6.5204 | 0.0021077 | 9.6388e-06 | 1 | 0
630 | 10.5 | 5.0013 | 12.0021 | 5 | 12 | 70.037 | 40 | -0.00212 | 3.574 | -1.227e-05 | -0.029492 | 4.8354 | 0 | 4.8059 |  | 15.2059 | 4 | 15.2059 | 70.037 | 35.0185 | 15 | 35 | 0.018497 | 6.5389 | 0.00212 | 7.6685e-06 | 1 | 0
631 | 10.5167 | 5.0013 | 12.0021 | 5 | 12 | 70.0182 | 40 | -0.0021291 | 3.5719 | -9.1409e-06 | -0.029619 | 4.8325 | 0 | 4.8029 |  | 15.2029 | 4 | 15.2029 | 70.0182 | 35.0091 | 15 | 35 | 0.0090983 | 6.548 | 0.0021291 | 5.7131e-06 | 1 | 0
632 | 10.5333 | 5.0013 | 12.0021 | 5 | 12 | 69.9996 | 40 | -0.0021352 | 3.5697 | -6.04e-06 | -0.029703 | 4.8296 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9996 | 34.9998 | 15 | 35 | -0.0001916 | 6.5478 | 0.0021352 | 3.775e-06 | 1 | 0
633 | 10.55 | 5.0013 | 12.0021 | 5 | 12 | 69.9813 | 40 | -0.0021381 | 3.5676 | -2.9709e-06 | -0.029745 | 4.8267 | 0 | 4.797 |  | 15.197 | 4 | 15.197 | 69.9813 | 34.9906 | 15 | 35 | -0.0093606 | 6.5385 | 0.0021381 | 1.8568e-06 | 1 | 0
634 | 10.5667 | 5.0013 | 12.0021 | 5 | 12 | 69.9632 | 40 | -0.0021381 | 3.5655 | 6.2562e-08 | -0.029744 | 4.8239 | 0 | 4.7941 |  | 15.1941 | 4 | 15.1941 | 69.9632 | 34.9816 | 15 | 35 | -0.018398 | 6.5201 | 0.0021381 | -3.9101e-08 | -1 | -2
635 | 10.5833 | 5.0013 | 12.0021 | 5 | 12 | 69.9454 | 40 | -0.002135 | 3.5633 | 3.0565e-06 | -0.029701 | 4.821 | 0 | 4.7913 |  | 15.1913 | 4 | 15.1913 | 69.9454 | 34.9727 | 15 | 35 | -0.027291 | 6.4928 | 0.002135 | -1.9103e-06 | -1 | 0
636 | 10.6 | 5.0013 | 12.0021 | 5 | 12 | 69.9279 | 40 | -0.002129 | 3.5612 | 6.0074e-06 | -0.029618 | 4.8181 | 0 | 4.7885 |  | 15.1885 | 4 | 15.1885 | 69.9279 | 34.964 | 15 | 35 | -0.036031 | 6.4567 | 0.002129 | -3.7546e-06 | -1 | 0
637 | 10.6167 | 5.0013 | 12.0021 | 5 | 12 | 69.9108 | 40 | -0.0021201 | 3.5591 | 8.9115e-06 | -0.029494 | 4.8152 | 0 | 4.7857 |  | 15.1857 | 4 | 15.1857 | 69.9108 | 34.9554 | 15 | 35 | -0.044608 | 6.4121 | 0.0021201 | -5.5697e-06 | -1 | 0
638 | 10.6333 | 5.0013 | 12.0021 | 5 | 12 | 69.894 | 40 | -0.0021083 | 3.557 | 1.1765e-05 | -0.02933 | 4.8124 | 0 | 4.783 |  | 15.183 | 4 | 15.183 | 69.894 | 34.947 | 15 | 35 | -0.05301 | 6.3591 | 0.0021083 | -7.3534e-06 | -1 | 0
639 | 10.65 | 5.0013 | 12.0021 | 5 | 12 | 69.8775 | 40 | -0.0020938 | 3.5549 | 1.4566e-05 | -0.029127 | 4.8095 | 0 | 4.7804 |  | 15.1804 | 4 | 15.1804 | 69.8775 | 34.9388 | 15 | 35 | -0.061229 | 6.2979 | 0.0020938 | -9.1036e-06 | -1 | 0
640 | 10.6667 | 5.0013 | 12.0021 | 5 | 12 | 69.8615 | 40 | -0.0020764 | 3.5528 | 1.7309e-05 | -0.028887 | 4.8067 | 0 | 4.7778 |  | 15.1778 | 4 | 15.1778 | 69.8615 | 34.9307 | 15 | 35 | -0.069256 | 6.2286 | 0.0020764 | -1.0818e-05 | -1 | 0
641 | 10.6833 | 5.0013 | 12.0021 | 5 | 12 | 69.8458 | 40 | -0.0020565 | 3.5507 | 1.9993e-05 | -0.028608 | 4.8039 | 0 | 4.7753 |  | 15.1753 | 4 | 15.1753 | 69.8458 | 34.9229 | 15 | 35 | -0.077081 | 6.1516 | 0.0020565 | -1.2496e-05 | -1 | 0
642 | 10.7 | 5.0013 | 12.002 | 5 | 12 | 69.8306 | 40 | -0.0020338 | 3.5487 | 2.2614e-05 | -0.028294 | 4.8012 | 0 | 4.7729 |  | 15.1729 | 4 | 15.1729 | 69.8306 | 34.9153 | 15 | 35 | -0.084697 | 6.0669 | 0.0020338 | -1.4134e-05 | -1 | 0
643 | 10.7167 | 5.0013 | 12.002 | 5 | 12 | 69.8158 | 40 | -0.0020087 | 3.5467 | 2.5169e-05 | -0.027944 | 4.7985 | 0 | 4.7705 |  | 15.1705 | 4 | 15.1705 | 69.8158 | 34.9079 | 15 | 35 | -0.092095 | 5.9748 | 0.0020087 | -1.5731e-05 | -1 | 0
644 | 10.7333 | 5.0012 | 12.002 | 5 | 12 | 69.8015 | 40 | -0.001981 | 3.5447 | 2.7656e-05 | -0.027559 | 4.7958 | 0 | 4.7682 |  | 15.1682 | 4 | 15.1682 | 69.8015 | 34.9007 | 15 | 35 | -0.099269 | 5.8755 | 0.001981 | -1.7285e-05 | -1 | 0
645 | 10.75 | 5.0012 | 12.002 | 5 | 12 | 69.7876 | 40 | -0.0019509 | 3.5428 | 3.0072e-05 | -0.027141 | 4.7932 | 0 | 4.766 |  | 15.166 | 4 | 15.166 | 69.7876 | 34.8938 | 15 | 35 | -0.10621 | 5.7693 | 0.0019509 | -1.8795e-05 | -1 | 0
646 | 10.7667 | 5.0012 | 12.0019 | 5 | 12 | 69.7742 | 40 | -0.0019185 | 3.5408 | 3.2414e-05 | -0.02669 | 4.7906 | 0 | 4.7639 |  | 15.1639 | 4 | 15.1639 | 69.7742 | 34.8871 | 15 | 35 | -0.11291 | 5.6564 | 0.0019185 | -2.0259e-05 | -1 | 0
647 | 10.7833 | 5.0012 | 12.0019 | 5 | 12 | 69.7613 | 40 | -0.0018838 | 3.539 | 3.4681e-05 | -0.026207 | 4.788 | 0 | 4.7618 |  | 15.1618 | 4 | 15.1618 | 69.7613 | 34.8806 | 15 | 35 | -0.11937 | 5.537 | 0.0018838 | -2.1675e-05 | -1 | 0
648 | 10.8 | 5.0012 | 12.0018 | 5 | 12 | 69.7488 | 40 | -0.001847 | 3.5371 | 3.6869e-05 | -0.025694 | 4.7855 | 0 | 4.7598 |  | 15.1598 | 4 | 15.1598 | 69.7488 | 34.8744 | 15 | 35 | -0.12558 | 5.4114 | 0.001847 | -2.3043e-05 | -1 | 0
649 | 10.8167 | 5.0011 | 12.0018 | 5 | 12 | 69.737 | 40 | -0.001808 | 3.5353 | 3.8978e-05 | -0.025152 | 4.7831 | 0 | 4.7579 |  | 15.1579 | 4 | 15.1579 | 69.737 | 34.8685 | 15 | 35 | -0.13152 | 5.2799 | 0.001808 | -2.4361e-05 | -1 | 0
650 | 10.8333 | 5.0011 | 12.0018 | 5 | 12 | 69.7256 | 40 | -0.001767 | 3.5335 | 4.1004e-05 | -0.024582 | 4.7807 | 0 | 4.7561 |  | 15.1561 | 4 | 15.1561 | 69.7256 | 34.8628 | 15 | 35 | -0.13721 | 5.1427 | 0.001767 | -2.5628e-05 | -1 | 0
651 | 10.85 | 5.0011 | 12.0017 | 5 | 12 | 69.7147 | 40 | -0.0017241 | 3.5318 | 4.2947e-05 | -0.023984 | 4.7783 | 0 | 4.7544 |  | 15.1544 | 4 | 15.1544 | 69.7147 | 34.8574 | 15 | 35 | -0.14264 | 5.0001 | 0.0017241 | -2.6842e-05 | -1 | 0
652 | 10.8667 | 5.001 | 12.0017 | 5 | 12 | 69.7044 | 40 | -0.0016792 | 3.5301 | 4.4804e-05 | -0.023361 | 4.7761 | 0 | 4.7527 |  | 15.1527 | 4 | 15.1527 | 69.7044 | 34.8522 | 15 | 35 | -0.14779 | 4.8523 | 0.0016792 | -2.8003e-05 | -1 | 0
653 | 10.8833 | 5.001 | 12.0016 | 5 | 12 | 69.6947 | 40 | -0.0016327 | 3.5285 | 4.6575e-05 | -0.022713 | 4.7739 | 0 | 4.7511 |  | 15.1511 | 4 | 15.1511 | 69.6947 | 34.8473 | 15 | 35 | -0.15267 | 4.6996 | 0.0016327 | -2.9109e-05 | -1 | 0
654 | 10.9 | 5.001 | 12.0016 | 5 | 12 | 69.6855 | 40 | -0.0015844 | 3.5269 | 4.8257e-05 | -0.022042 | 4.7717 | 0 | 4.7497 |  | 15.1497 | 4 | 15.1497 | 69.6855 | 34.8427 | 15 | 35 | -0.15727 | 4.5423 | 0.0015844 | -3.0161e-05 | -1 | 0
655 | 10.9167 | 5.001 | 12.0015 | 5 | 12 | 69.6768 | 40 | -0.0015346 | 3.5254 | 4.985e-05 | -0.021348 | 4.7696 | 0 | 4.7483 |  | 15.1483 | 4 | 15.1483 | 69.6768 | 34.8384 | 15 | 35 | -0.16159 | 4.3808 | 0.0015346 | -3.1156e-05 | -1 | 0
656 | 10.9333 | 5.0009 | 12.0015 | 5 | 12 | 69.6687 | 40 | -0.0014832 | 3.5239 | 5.1352e-05 | -0.020634 | 4.7676 | 0 | 4.747 |  | 15.147 | 4 | 15.147 | 69.6687 | 34.8344 | 15 | 35 | -0.16563 | 4.2151 | 0.0014832 | -3.2095e-05 | -1 | 0
657 | 10.95 | 5.0009 | 12.0014 | 5 | 12 | 69.6612 | 40 | -0.0014304 | 3.5225 | 5.2763e-05 | -0.0199 | 4.7657 | 0 | 4.7458 |  | 15.1458 | 4 | 15.1458 | 69.6612 | 34.8306 | 15 | 35 | -0.16938 | 4.0457 | 0.0014304 | -3.2977e-05 | -1 | 0
658 | 10.9667 | 5.0009 | 12.0014 | 5 | 12 | 69.6543 | 40 | -0.0013764 | 3.5211 | 5.4082e-05 | -0.019147 | 4.7638 | 0 | 4.7447 |  | 15.1447 | 4 | 15.1447 | 69.6543 | 34.8272 | 15 | 35 | -0.17285 | 3.8729 | 0.0013764 | -3.3801e-05 | -1 | 0
659 | 10.9833 | 5.0008 | 12.0013 | 5 | 12 | 69.6479 | 40 | -0.0013211 | 3.5198 | 5.5308e-05 | -0.018378 | 4.762 | 0 | 4.7437 |  | 15.1437 | 4 | 15.1437 | 69.6479 | 34.824 | 15 | 35 | -0.17603 | 3.6969 | 0.0013211 | -3.4567e-05 | -1 | 0
660 | 11 | 5.0008 | 12.0013 | 5 | 12 | 69.6422 | 40 | -0.0012646 | 3.5185 | 5.644e-05 | -0.017593 | 4.7603 | 0 | 4.7427 |  | 15.1427 | 4 | 15.1427 | 69.6422 | 34.8211 | 15 | 35 | -0.17892 | 3.5179 | 0.0012646 | -3.5275e-05 | -1 | 0
661 | 11.0167 | 5.0008 | 12.0012 | 5 | 12 | 69.6369 | 40 | -0.0012071 | 3.5173 | 5.7479e-05 | -0.016793 | 4.7587 | 0 | 4.7419 |  | 15.1419 | 4 | 15.1419 | 69.6369 | 34.8185 | 15 | 35 | -0.18153 | 3.3364 | 0.0012071 | -3.5924e-05 | -1 | 0
662 | 11.0333 | 5.0007 | 12.0011 | 5 | 12 | 69.6323 | 40 | -0.0011487 | 3.5162 | 5.8423e-05 | -0.01598 | 4.7572 | 0 | 4.7412 |  | 15.1412 | 4 | 15.1412 | 69.6323 | 34.8162 | 15 | 35 | -0.18384 | 3.1526 | 0.0011487 | -3.6515e-05 | -1 | 0
663 | 11.05 | 5.0007 | 12.0011 | 5 | 12 | 69.6283 | 40 | -0.0010894 | 3.5151 | 5.9274e-05 | -0.015156 | 4.7557 | 0 | 4.7405 |  | 15.1405 | 4 | 15.1405 | 69.6283 | 34.8141 | 15 | 35 | -0.18587 | 2.9667 | 0.0010894 | -3.7046e-05 | -1 | 0
664 | 11.0667 | 5.0006 | 12.001 | 5 | 12 | 69.6248 | 40 | -0.0010294 | 3.514 | 6.003e-05 | -0.014321 | 4.7543 | 0 | 4.74 |  | 15.14 | 4 | 15.14 | 69.6248 | 34.8124 | 15 | 35 | -0.18762 | 2.7791 | 0.0010294 | -3.7519e-05 | -1 | 0
665 | 11.0833 | 5.0006 | 12.001 | 5 | 12 | 69.6219 | 40 | -0.00096872 | 3.5131 | 6.0693e-05 | -0.013476 | 4.753 | 0 | 4.7395 |  | 15.1395 | 4 | 15.1395 | 69.6219 | 34.8109 | 15 | 35 | -0.18907 | 2.59 | 0.00096872 | -3.7933e-05 | -1 | 0
666 | 11.1 | 5.0006 | 12.0009 | 5 | 12 | 69.6195 | 40 | -0.00090746 | 3.5122 | 6.1262e-05 | -0.012624 | 4.7517 | 0 | 4.7391 |  | 15.1391 | 4 | 15.1391 | 69.6195 | 34.8098 | 15 | 35 | -0.19025 | 2.3998 | 0.00090746 | -3.8289e-05 | -1 | 0
667 | 11.1167 | 5.0005 | 12.0008 | 5 | 12 | 69.6177 | 40 | -0.00084572 | 3.5113 | 6.1738e-05 | -0.011765 | 4.7506 | 0 | 4.7388 |  | 15.1388 | 4 | 15.1388 | 69.6177 | 34.8089 | 15 | 35 | -0.19114 | 2.2086 | 0.00084572 | -3.8586e-05 | -1 | 0
668 | 11.1333 | 5.0005 | 12.0008 | 5 | 12 | 69.6165 | 40 | -0.0007836 | 3.5105 | 6.2121e-05 | -0.010901 | 4.7495 | 0 | 4.7386 |  | 15.1386 | 4 | 15.1386 | 69.6165 | 34.8083 | 15 | 35 | -0.19175 | 2.0169 | 0.0007836 | -3.8826e-05 | -1 | 0
669 | 11.15 | 5.0005 | 12.0007 | 5 | 12 | 69.6158 | 40 | -0.00072119 | 3.5098 | 6.2412e-05 | -0.010033 | 4.7486 | 0 | 4.7385 |  | 15.1385 | 4 | 15.1385 | 69.6158 | 34.8079 | 15 | 35 | -0.19209 | 1.8248 | 0.00072119 | -3.9008e-05 | -1 | 0
670 | 11.1667 | 5.0004 | 12.0007 | 5 | 12 | 69.6157 | 40 | -0.00065858 | 3.5092 | 6.2612e-05 | -0.0091618 | 4.7477 | 0 | 4.7385 |  | 15.1385 | 4 | 15.1385 | 69.6157 | 34.8079 | 15 | 35 | -0.19215 | 1.6327 | 0.00065858 | -3.9133e-05 | -1 | 0
671 | 11.1833 | 5.0004 | 12.0006 | 5 | 12 | 69.6161 | 40 | -0.00059585 | 3.5086 | 6.2722e-05 | -0.0082893 | 4.7469 | 0 | 4.7386 |  | 15.1386 | 4 | 15.1386 | 69.6161 | 34.8081 | 15 | 35 | -0.19194 | 1.4407 | 0.00059585 | -3.9201e-05 | -1 | 0
672 | 11.2 | 5.0003 | 12.0005 | 5 | 12 | 69.6171 | 40 | -0.00053311 | 3.508 | 6.2742e-05 | -0.0074164 | 4.7461 | 0 | 4.7387 |  | 15.1387 | 4 | 15.1387 | 69.6171 | 34.8085 | 15 | 35 | -0.19147 | 1.2492 | 0.00053311 | -3.9214e-05 | -1 | 0
673 | 11.2167 | 5.0003 | 12.0005 | 5 | 12 | 69.6185 | 40 | -0.00047044 | 3.5076 | 6.2674e-05 | -0.0065445 | 4.7455 | 0 | 4.739 |  | 15.139 | 4 | 15.139 | 69.6185 | 34.8093 | 15 | 35 | -0.19073 | 1.0585 | 0.00047044 | -3.9172e-05 | -1 | 0
674 | 11.2333 | 5.0003 | 12.0004 | 5 | 12 | 69.6205 | 40 | -0.00040792 | 3.5071 | 6.252e-05 | -0.0056748 | 4.745 | 0 | 4.7393 |  | 15.1393 | 4 | 15.1393 | 69.6205 | 34.8103 | 15 | 35 | -0.18974 | 0.86878 | 0.00040792 | -3.9075e-05 | -1 | 0
675 | 11.25 | 5.0002 | 12.0003 | 5 | 12 | 69.623 | 40 | -0.00034564 | 3.5068 | 6.228e-05 | -0.0048084 | 4.7445 | 0 | 4.7397 |  | 15.1397 | 4 | 15.1397 | 69.623 | 34.8115 | 15 | 35 | -0.18849 | 0.68029 | 0.00034564 | -3.8925e-05 | -1 | 0
676 | 11.2667 | 5.0002 | 12.0003 | 5 | 12 | 69.626 | 40 | -0.00028368 | 3.5065 | 6.1955e-05 | -0.0039465 | 4.7441 | 0 | 4.7402 |  | 15.1402 | 4 | 15.1402 | 69.626 | 34.813 | 15 | 35 | -0.187 | 0.49329 | 0.00028368 | -3.8722e-05 | -1 | 0
677 | 11.2833 | 5.0001 | 12.0002 | 5 | 12 | 69.6295 | 40 | -0.00022213 | 3.5063 | 6.1548e-05 | -0.0030902 | 4.7438 | 0 | 4.7407 |  | 15.1407 | 4 | 15.1407 | 69.6295 | 34.8147 | 15 | 35 | -0.18526 | 0.30803 | 0.00022213 | -3.8468e-05 | -1 | 0
678 | 11.3 | 5.0001 | 12.0002 | 5 | 12 | 69.6334 | 40 | -0.00016107 | 3.5061 | 6.106e-05 | -0.0022408 | 4.7436 | 0 | 4.7413 |  | 15.1413 | 4 | 15.1413 | 69.6334 | 34.8167 | 15 | 35 | -0.18329 | 0.12474 | 0.00016107 | -3.8163e-05 | -1 | 0
679 | 11.3167 | 5.0001 | 12.0001 | 5 | 12 | 69.6378 | 40 | -0.00010058 | 3.506 | 6.0493e-05 | -0.0013992 | 4.7435 | 0 | 4.7421 |  | 15.1421 | 4 | 15.1421 | 69.6378 | 34.8189 | 15 | 35 | -0.18108 | -0.056343 | 0.00010058 | -3.7808e-05 | -1 | 0
680 | 11.3333 | 5 | 12 | 5 | 12 | 69.6427 | 40 | -4.0731e-05 | 3.506 | 5.9849e-05 | -0.00056664 | 4.7434 | 0 | 4.7428 |  | 15.1428 | 4 | 15.1428 | 69.6427 | 34.8213 | 15 | 35 | -0.17865 | -0.235 | 4.0731e-05 | -3.7406e-05 | -1 | 0
681 | 11.35 | 5 | 12 | 5 | 12 | 69.648 | 40 | 1.8398e-05 | 3.506 | 5.9129e-05 | 0.00025594 | 4.7434 | 0 | 4.7437 |  | 15.1437 | 4 | 15.1437 | 69.648 | 34.824 | 15 | 35 | -0.176 | -0.411 | 1.8398e-05 | -3.6956e-05 | -1 | 0
682 | 11.3667 | 5 | 11.9999 | 5 | 12 | 69.6537 | 40 | 7.6734e-05 | 3.5061 | 5.8336e-05 | 0.0010675 | 4.7435 | 0 | 4.7446 |  | 15.1446 | 4 | 15.1446 | 69.6537 | 34.8269 | 15 | 35 | -0.17314 | -0.58415 | 7.6734e-05 | -3.646e-05 | -1 | 0
683 | 11.3833 | 4.9999 | 11.9999 | 5 | 12 | 69.6598 | 40 | 0.0001342 | 3.5062 | 5.7471e-05 | 0.001867 | 4.7437 | 0 | 4.7456 |  | 15.1456 | 4 | 15.1456 | 69.6598 | 34.8299 | 15 | 35 | -0.17008 | -0.75422 | 0.0001342 | -3.5919e-05 | -1 | 0
684 | 11.4 | 4.9999 | 11.9998 | 5 | 12 | 69.6664 | 40 | 0.00019074 | 3.5064 | 5.6537e-05 | 0.0026535 | 4.744 | 0 | 4.7466 |  | 15.1466 | 4 | 15.1466 | 69.6664 | 34.8332 | 15 | 35 | -0.16681 | -0.92104 | 0.00019074 | -3.5336e-05 | -1 | 0
685 | 11.4167 | 4.9998 | 11.9998 | 5 | 12 | 69.6733 | 40 | 0.00024628 | 3.5067 | 5.5536e-05 | 0.0034261 | 4.7443 | 0 | 4.7477 |  | 15.1477 | 4 | 15.1477 | 69.6733 | 34.8366 | 15 | 35 | -0.16336 | -1.0844 | 0.00024628 | -3.471e-05 | -1 | 0
686 | 11.4333 | 4.9998 | 11.9997 | 5 | 12 | 69.6806 | 40 | 0.00030075 | 3.507 | 5.447e-05 | 0.0041839 | 4.7447 | 0 | 4.7489 |  | 15.1489 | 4 | 15.1489 | 69.6806 | 34.8403 | 15 | 35 | -0.15972 | -1.2441 | 0.00030075 | -3.4044e-05 | -1 | 0
687 | 11.45 | 4.9998 | 11.9996 | 5 | 12 | 69.6882 | 40 | 0.00035409 | 3.5073 | 5.3342e-05 | 0.0049259 | 4.7452 | 0 | 4.7501 |  | 15.1501 | 4 | 15.1501 | 69.6882 | 34.8441 | 15 | 35 | -0.1559 | -1.4 | 0.00035409 | -3.3339e-05 | -1 | 0
688 | 11.4667 | 4.9997 | 11.9996 | 5 | 12 | 69.6962 | 40 | 0.00040624 | 3.5077 | 5.2153e-05 | 0.0056515 | 4.7457 | 0 | 4.7514 |  | 15.1514 | 4 | 15.1514 | 69.6962 | 34.8481 | 15 | 35 | -0.15192 | -1.5519 | 0.00040624 | -3.2596e-05 | -1 | 0
689 | 11.4833 | 4.9997 | 11.9995 | 5 | 12 | 69.7045 | 40 | 0.00045715 | 3.5082 | 5.0907e-05 | 0.0063597 | 4.7464 | 0 | 4.7527 |  | 15.1527 | 4 | 15.1527 | 69.7045 | 34.8522 | 15 | 35 | -0.14777 | -1.6997 | 0.00045715 | -3.1817e-05 | -1 | 0
690 | 11.5 | 4.9997 | 11.9995 | 5 | 12 | 69.7131 | 40 | 0.00050676 | 3.5087 | 4.9606e-05 | 0.0070498 | 4.747 | 0 | 4.7541 |  | 15.1541 | 4 | 15.1541 | 69.7131 | 34.8565 | 15 | 35 | -0.14347 | -1.8432 | 0.00050676 | -3.1004e-05 | -1 | 0
691 | 11.5167 | 4.9997 | 11.9994 | 5 | 12 | 69.7219 | 40 | 0.00055501 | 3.5092 | 4.8252e-05 | 0.007721 | 4.7478 | 0 | 4.7555 |  | 15.1555 | 4 | 15.1555 | 69.7219 | 34.861 | 15 | 35 | -0.13903 | -1.9822 | 0.00055501 | -3.0158e-05 | -1 | 0
692 | 11.5333 | 4.9996 | 11.9994 | 5 | 12 | 69.7311 | 40 | 0.00060186 | 3.5098 | 4.6848e-05 | 0.0083728 | 4.7486 | 0 | 4.757 |  | 15.157 | 4 | 15.157 | 69.7311 | 34.8656 | 15 | 35 | -0.13445 | -2.1167 | 0.00060186 | -2.928e-05 | -1 | 0
693 | 11.55 | 4.9996 | 11.9994 | 5 | 12 | 69.7405 | 40 | 0.00064725 | 3.5105 | 4.5397e-05 | 0.0090043 | 4.7495 | 0 | 4.7585 |  | 15.1585 | 4 | 15.1585 | 69.7405 | 34.8703 | 15 | 35 | -0.12974 | -2.2464 | 0.00064725 | -2.8373e-05 | -1 | 0
694 | 11.5667 | 4.9996 | 11.9993 | 5 | 12 | 69.7502 | 40 | 0.00069115 | 3.5112 | 4.3901e-05 | 0.009615 | 4.7504 | 0 | 4.76 |  | 15.16 | 4 | 15.16 | 69.7502 | 34.8751 | 15 | 35 | -0.12491 | -2.3713 | 0.00069115 | -2.7438e-05 | -1 | 0
695 | 11.5833 | 4.9995 | 11.9993 | 5 | 12 | 69.7601 | 40 | 0.00073352 | 3.5119 | 4.2363e-05 | 0.010204 | 4.7514 | 0 | 4.7616 |  | 15.1616 | 4 | 15.1616 | 69.7601 | 34.88 | 15 | 35 | -0.11996 | -2.4913 | 0.00073352 | -2.6477e-05 | -1 | 0
696 | 11.6 | 4.9995 | 11.9992 | 5 | 12 | 69.7702 | 40 | 0.0007743 | 3.5127 | 4.0786e-05 | 0.010772 | 4.7525 | 0 | 4.7632 |  | 15.1632 | 4 | 15.1632 | 69.7702 | 34.8851 | 15 | 35 | -0.11492 | -2.6062 | 0.0007743 | -2.5491e-05 | -1 | 0
697 | 11.6167 | 4.9995 | 11.9992 | 5 | 12 | 69.7805 | 40 | 0.00081348 | 3.5135 | 3.9172e-05 | 0.011317 | 4.7536 | 0 | 4.7649 |  | 15.1649 | 4 | 15.1649 | 69.7805 | 34.8902 | 15 | 35 | -0.10977 | -2.716 | 0.00081348 | -2.4482e-05 | -1 | 0
698 | 11.6333 | 4.9995 | 11.9991 | 5 | 12 | 69.7909 | 40 | 0.000851 | 3.5143 | 3.7524e-05 | 0.011839 | 4.7547 | 0 | 4.7665 |  | 15.1665 | 4 | 15.1665 | 69.7909 | 34.8955 | 15 | 35 | -0.10455 | -2.8205 | 0.000851 | -2.3452e-05 | -1 | 0
699 | 11.65 | 4.9994 | 11.9991 | 5 | 12 | 69.8015 | 40 | 0.00088684 | 3.5152 | 3.5845e-05 | 0.012337 | 4.7559 | 0 | 4.7682 |  | 15.1682 | 4 | 15.1682 | 69.8015 | 34.9008 | 15 | 35 | -0.099238 | -2.9197 | 0.00088684 | -2.2403e-05 | -1 | 0
700 | 11.6667 | 4.9994 | 11.9991 | 5 | 12 | 69.8123 | 40 | 0.00092098 | 3.5162 | 3.4137e-05 | 0.012812 | 4.7572 | 0 | 4.77 |  | 15.17 | 4 | 15.17 | 69.8123 | 34.9061 | 15 | 35 | -0.09386 | -3.0136 | 0.00092098 | -2.1336e-05 | -1 | 0
701 | 11.6833 | 4.9994 | 11.999 | 5 | 12 | 69.8232 | 40 | 0.00095339 | 3.5171 | 3.2404e-05 | 0.013263 | 4.7584 | 0 | 4.7717 |  | 15.1717 | 4 | 15.1717 | 69.8232 | 34.9116 | 15 | 35 | -0.08842 | -3.102 | 0.00095339 | -2.0253e-05 | -1 | 0
702 | 11.7 | 4.9994 | 11.999 | 5 | 12 | 69.8341 | 40 | 0.00098403 | 3.5181 | 3.0648e-05 | 0.013689 | 4.7598 | 0 | 4.7735 |  | 15.1735 | 4 | 15.1735 | 69.8341 | 34.9171 | 15 | 35 | -0.082927 | -3.185 | 0.00098403 | -1.9155e-05 | -1 | 0
703 | 11.7167 | 4.9994 | 11.999 | 5 | 12 | 69.8452 | 40 | 0.0010129 | 3.5191 | 2.8872e-05 | 0.014091 | 4.7611 | 0 | 4.7752 |  | 15.1752 | 4 | 15.1752 | 69.8452 | 34.9226 | 15 | 35 | -0.07739 | -3.2623 | 0.0010129 | -1.8045e-05 | -1 | 0
704 | 11.7333 | 4.9994 | 11.999 | 5 | 12 | 69.8564 | 40 | 0.00104 | 3.5201 | 2.7078e-05 | 0.014468 | 4.7626 | 0 | 4.777 |  | 15.177 | 4 | 15.177 | 69.8564 | 34.9282 | 15 | 35 | -0.071816 | -3.3342 | 0.00104 | -1.6924e-05 | -1 | 0
705 | 11.75 | 4.9993 | 11.9989 | 5 | 12 | 69.8676 | 40 | 0.0010653 | 3.5212 | 2.527e-05 | 0.014819 | 4.764 | 0 | 4.7788 |  | 15.1788 | 4 | 15.1788 | 69.8676 | 34.9338 | 15 | 35 | -0.066213 | -3.4004 | 0.0010653 | -1.5794e-05 | -1 | 0
706 | 11.7667 | 4.9993 | 11.9989 | 5 | 12 | 69.8788 | 40 | 0.0010887 | 3.5223 | 2.345e-05 | 0.015146 | 4.7655 | 0 | 4.7806 |  | 15.1806 | 4 | 15.1806 | 69.8788 | 34.9394 | 15 | 35 | -0.060591 | -3.461 | 0.0010887 | -1.4656e-05 | -1 | 0
707 | 11.7833 | 4.9993 | 11.9989 | 5 | 12 | 69.8901 | 40 | 0.0011103 | 3.5234 | 2.1621e-05 | 0.015446 | 4.767 | 0 | 4.7824 |  | 15.1824 | 4 | 15.1824 | 69.8901 | 34.945 | 15 | 35 | -0.054956 | -3.5159 | 0.0011103 | -1.3513e-05 | -1 | 0
708 | 11.8 | 4.9993 | 11.9989 | 5 | 12 | 69.9014 | 40 | 0.0011301 | 3.5245 | 1.9785e-05 | 0.015722 | 4.7685 | 0 | 4.7842 |  | 15.1842 | 4 | 15.1842 | 69.9014 | 34.9507 | 15 | 35 | -0.049318 | -3.5652 | 0.0011301 | -1.2365e-05 | -1 | 0
709 | 11.8167 | 4.9993 | 11.9989 | 5 | 12 | 69.9126 | 40 | 0.0011481 | 3.5257 | 1.7945e-05 | 0.015971 | 4.77 | 0 | 4.786 |  | 15.186 | 4 | 15.186 | 69.9126 | 34.9563 | 15 | 35 | -0.043684 | -3.6089 | 0.0011481 | -1.1216e-05 | -1 | 0
710 | 11.8333 | 4.9993 | 11.9988 | 5 | 12 | 69.9239 | 40 | 0.0011642 | 3.5269 | 1.6104e-05 | 0.016195 | 4.7716 | 0 | 4.7878 |  | 15.1878 | 4 | 15.1878 | 69.9239 | 34.9619 | 15 | 35 | -0.038062 | -3.647 | 0.0011642 | -1.0065e-05 | -1 | 0
711 | 11.85 | 4.9993 | 11.9988 | 5 | 12 | 69.9351 | 40 | 0.0011784 | 3.528 | 1.4264e-05 | 0.016394 | 4.7732 | 0 | 4.7896 |  | 15.1896 | 4 | 15.1896 | 69.9351 | 34.9675 | 15 | 35 | -0.03246 | -3.6794 | 0.0011784 | -8.9151e-06 | -1 | 0
712 | 11.8667 | 4.9993 | 11.9988 | 5 | 12 | 69.9462 | 40 | 0.0011909 | 3.5292 | 1.2428e-05 | 0.016567 | 4.7748 | 0 | 4.7914 |  | 15.1914 | 4 | 15.1914 | 69.9462 | 34.9731 | 15 | 35 | -0.026885 | -3.7063 | 0.0011909 | -7.7678e-06 | -1 | 0
713 | 11.8833 | 4.9992 | 11.9988 | 5 | 12 | 69.9573 | 40 | 0.0012015 | 3.5304 | 1.0599e-05 | 0.016714 | 4.7765 | 0 | 4.7932 |  | 15.1932 | 4 | 15.1932 | 69.9573 | 34.9787 | 15 | 35 | -0.021344 | -3.7277 | 0.0012015 | -6.6244e-06 | -1 | 0
714 | 11.9 | 4.9992 | 11.9988 | 5 | 12 | 69.9683 | 40 | 0.0012102 | 3.5316 | 8.7786e-06 | 0.016836 | 4.7781 | 0 | 4.7949 |  | 15.1949 | 4 | 15.1949 | 69.9683 | 34.9842 | 15 | 35 | -0.015846 | -3.7435 | 0.0012102 | -5.4866e-06 | -1 | 0
715 | 11.9167 | 4.9992 | 11.9988 | 5 | 12 | 69.9792 | 40 | 0.0012172 | 3.5329 | 6.9695e-06 | 0.016933 | 4.7797 | 0 | 4.7967 |  | 15.1967 | 4 | 15.1967 | 69.9792 | 34.9896 | 15 | 35 | -0.010396 | -3.7539 | 0.0012172 | -4.3559e-06 | -1 | 0
716 | 11.9333 | 4.9992 | 11.9988 | 5 | 12 | 69.99 | 40 | 0.0012224 | 3.5341 | 5.1741e-06 | 0.017005 | 4.7814 | 0 | 4.7984 |  | 15.1984 | 4 | 15.1984 | 69.99 | 34.995 | 15 | 35 | -0.0050034 | -3.7589 | 0.0012224 | -3.2338e-06 | -1 | 0
717 | 11.95 | 4.9992 | 11.9988 | 5 | 12 | 70.0007 | 40 | 0.0012258 | 3.5353 | 3.3948e-06 | 0.017052 | 4.7831 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0007 | 35.0003 | 15 | 35 | 0.00032667 | -3.7586 | 0.0012258 | -2.1217e-06 | -1 | 0
718 | 11.9667 | 4.9992 | 11.9988 | 5 | 12 | 70.0112 | 40 | 0.0012274 | 3.5365 | 1.6338e-06 | 0.017075 | 4.7847 | 0 | 4.8018 |  | 15.2018 | 4 | 15.2018 | 70.0112 | 35.0056 | 15 | 35 | 0.0055871 | -3.753 | 0.0012274 | -1.0211e-06 | -1 | 0
719 | 11.9833 | 4.9992 | 11.9988 | 5 | 12 | 70.0215 | 40 | 0.0012273 | 3.5378 | -1.0667e-07 | 0.017074 | 4.7864 | 0 | 4.8034 |  | 15.2034 | 4 | 15.2034 | 70.0215 | 35.0108 | 15 | 35 | 0.010771 | -3.7422 | 0.0012273 | 6.6668e-08 | 1 | 2
720 | 12 | 4.9992 | 11.9988 | 5 | 12 | 70.0317 | 40 | 0.0012255 | 3.539 | -1.8244e-06 | 0.017048 | 4.788 | 0 | 4.8051 |  | 15.2051 | 4 | 15.2051 | 70.0317 | 35.0159 | 15 | 35 | 0.015873 | -3.7264 | 0.0012255 | 1.1402e-06 | 1 | 0
721 | 12.0167 | 4.9992 | 11.9988 | 5 | 12 | 70.0418 | 40 | 0.001222 | 3.5402 | -3.5172e-06 | 0.016999 | 4.7897 | 0 | 4.8067 |  | 15.2067 | 4 | 15.2067 | 70.0418 | 35.0209 | 15 | 35 | 0.020887 | -3.7055 | 0.001222 | 2.1982e-06 | 1 | 0
722 | 12.0333 | 4.9992 | 11.9988 | 5 | 12 | 70.0516 | 40 | 0.0012168 | 3.5414 | -5.1831e-06 | 0.016927 | 4.7913 | 0 | 4.8083 |  | 15.2083 | 4 | 15.2083 | 70.0516 | 35.0258 | 15 | 35 | 0.025806 | -3.6797 | 0.0012168 | 3.2394e-06 | 1 | 0
723 | 12.05 | 4.9992 | 11.9988 | 5 | 12 | 70.0612 | 40 | 0.0012099 | 3.5426 | -6.8201e-06 | 0.016832 | 4.793 | 0 | 4.8098 |  | 15.2098 | 4 | 15.2098 | 70.0612 | 35.0306 | 15 | 35 | 0.030625 | -3.649 | 0.0012099 | 4.2626e-06 | 1 | 0
724 | 12.0667 | 4.9992 | 11.9988 | 5 | 12 | 70.0707 | 40 | 0.0012015 | 3.5438 | -8.4264e-06 | 0.016715 | 4.7946 | 0 | 4.8113 |  | 15.2113 | 4 | 15.2113 | 70.0707 | 35.0353 | 15 | 35 | 0.035339 | -3.6137 | 0.0012015 | 5.2665e-06 | 1 | 0
725 | 12.0833 | 4.9993 | 11.9988 | 5 | 12 | 70.0799 | 40 | 0.0011915 | 3.545 | -1e-05 | 0.016576 | 4.7962 | 0 | 4.8128 |  | 15.2128 | 4 | 15.2128 | 70.0799 | 35.0399 | 15 | 35 | 0.039942 | -3.5738 | 0.0011915 | 6.25e-06 | 1 | 0
726 | 12.1 | 4.9993 | 11.9988 | 5 | 12 | 70.0889 | 40 | 0.00118 | 3.5462 | -1.1539e-05 | 0.016415 | 4.7978 | 0 | 4.8142 |  | 15.2142 | 4 | 15.2142 | 70.0889 | 35.0444 | 15 | 35 | 0.044429 | -3.5293 | 0.00118 | 7.2119e-06 | 1 | 0
727 | 12.1167 | 4.9993 | 11.9988 | 5 | 12 | 70.0976 | 40 | 0.0011669 | 3.5474 | -1.3042e-05 | 0.016234 | 4.7994 | 0 | 4.8156 |  | 15.2156 | 4 | 15.2156 | 70.0976 | 35.0488 | 15 | 35 | 0.048796 | -3.4805 | 0.0011669 | 8.1513e-06 | 1 | 0
728 | 12.1333 | 4.9993 | 11.9988 | 5 | 12 | 70.1061 | 40 | 0.0011524 | 3.5485 | -1.4507e-05 | 0.016032 | 4.8009 | 0 | 4.817 |  | 15.217 | 4 | 15.217 | 70.1061 | 35.053 | 15 | 35 | 0.053037 | -3.4275 | 0.0011524 | 9.0671e-06 | 1 | 0
729 | 12.15 | 4.9993 | 11.9989 | 5 | 12 | 70.1143 | 40 | 0.0011365 | 3.5497 | -1.5933e-05 | 0.015811 | 4.8025 | 0 | 4.8183 |  | 15.2183 | 4 | 15.2183 | 70.1143 | 35.0571 | 15 | 35 | 0.05715 | -3.3703 | 0.0011365 | 9.9583e-06 | 1 | 0
730 | 12.1667 | 4.9993 | 11.9989 | 5 | 12 | 70.1223 | 40 | 0.0011192 | 3.5508 | -1.7318e-05 | 0.01557 | 4.804 | 0 | 4.8196 |  | 15.2196 | 4 | 15.2196 | 70.1223 | 35.0611 | 15 | 35 | 0.061129 | -3.3092 | 0.0011192 | 1.0824e-05 | 1 | 0
731 | 12.1833 | 4.9993 | 11.9989 | 5 | 12 | 70.1299 | 40 | 0.0011005 | 3.5519 | -1.8661e-05 | 0.01531 | 4.8055 | 0 | 4.8208 |  | 15.2208 | 4 | 15.2208 | 70.1299 | 35.065 | 15 | 35 | 0.06497 | -3.2442 | 0.0011005 | 1.1663e-05 | 1 | 0
732 | 12.2 | 4.9993 | 11.9989 | 5 | 12 | 70.1373 | 40 | 0.0010806 | 3.553 | -1.996e-05 | 0.015032 | 4.8069 | 0 | 4.822 |  | 15.222 | 4 | 15.222 | 70.1373 | 35.0687 | 15 | 35 | 0.068671 | -3.1756 | 0.0010806 | 1.2475e-05 | 1 | 0
733 | 12.2167 | 4.9993 | 11.9989 | 5 | 12 | 70.1445 | 40 | 0.0010593 | 3.554 | -2.1215e-05 | 0.014737 | 4.8084 | 0 | 4.8231 |  | 15.2231 | 4 | 15.2231 | 70.1445 | 35.0722 | 15 | 35 | 0.072228 | -3.1034 | 0.0010593 | 1.3259e-05 | 1 | 0
734 | 12.2333 | 4.9994 | 11.999 | 5 | 12 | 70.1513 | 40 | 0.0010369 | 3.5551 | -2.2423e-05 | 0.014425 | 4.8098 | 0 | 4.8242 |  | 15.2242 | 4 | 15.2242 | 70.1513 | 35.0756 | 15 | 35 | 0.075637 | -3.0277 | 0.0010369 | 1.4015e-05 | 1 | 0
735 | 12.25 | 4.9994 | 11.999 | 5 | 12 | 70.1578 | 40 | 0.0010133 | 3.5561 | -2.3585e-05 | 0.014097 | 4.8111 | 0 | 4.8252 |  | 15.2252 | 4 | 15.2252 | 70.1578 | 35.0789 | 15 | 35 | 0.078896 | -2.9488 | 0.0010133 | 1.474e-05 | 1 | 0
736 | 12.2667 | 4.9994 | 11.999 | 5 | 12 | 70.164 | 40 | 0.00098864 | 3.5571 | -2.4698e-05 | 0.013754 | 4.8125 | 0 | 4.8262 |  | 15.2262 | 4 | 15.2262 | 70.164 | 35.082 | 15 | 35 | 0.082002 | -2.8668 | 0.00098864 | 1.5436e-05 | 1 | 0
737 | 12.2833 | 4.9994 | 11.999 | 5 | 12 | 70.1699 | 40 | 0.00096288 | 3.558 | -2.5762e-05 | 0.013395 | 4.8138 | 0 | 4.8272 |  | 15.2272 | 4 | 15.2272 | 70.1699 | 35.085 | 15 | 35 | 0.084953 | -2.7819 | 0.00096288 | 1.6101e-05 | 1 | 0
738 | 12.3 | 4.9994 | 11.9991 | 5 | 12 | 70.1755 | 40 | 0.0009361 | 3.559 | -2.6776e-05 | 0.013023 | 4.8151 | 0 | 4.8281 |  | 15.2281 | 4 | 15.2281 | 70.1755 | 35.0877 | 15 | 35 | 0.087747 | -2.6941 | 0.0009361 | 1.6735e-05 | 1 | 0
739 | 12.3167 | 4.9994 | 11.9991 | 5 | 12 | 70.1808 | 40 | 0.00090836 | 3.5599 | -2.774e-05 | 0.012637 | 4.8163 | 0 | 4.8289 |  | 15.2289 | 4 | 15.2289 | 70.1808 | 35.0904 | 15 | 35 | 0.090381 | -2.6037 | 0.00090836 | 1.7337e-05 | 1 | 0
740 | 12.3333 | 4.9995 | 11.9991 | 5 | 12 | 70.1857 | 40 | 0.00087971 | 3.5607 | -2.8652e-05 | 0.012238 | 4.8175 | 0 | 4.8297 |  | 15.2297 | 4 | 15.2297 | 70.1857 | 35.0929 | 15 | 35 | 0.092855 | -2.5109 | 0.00087971 | 1.7908e-05 | 1 | 0
741 | 12.35 | 4.9995 | 11.9991 | 5 | 12 | 70.1903 | 40 | 0.0008502 | 3.5616 | -2.9512e-05 | 0.011828 | 4.8186 | 0 | 4.8305 |  | 15.2305 | 4 | 15.2305 | 70.1903 | 35.0952 | 15 | 35 | 0.095167 | -2.4157 | 0.0008502 | 1.8445e-05 | 1 | 0
742 | 12.3667 | 4.9995 | 11.9992 | 5 | 12 | 70.1946 | 40 | 0.00081988 | 3.5624 | -3.032e-05 | 0.011406 | 4.8197 | 0 | 4.8311 |  | 15.2311 | 4 | 15.2311 | 70.1946 | 35.0973 | 15 | 35 | 0.097315 | -2.3184 | 0.00081988 | 1.895e-05 | 1 | 0
743 | 12.3833 | 4.9995 | 11.9992 | 5 | 12 | 70.1986 | 40 | 0.0007888 | 3.5632 | -3.1075e-05 | 0.010973 | 4.8208 | 0 | 4.8318 |  | 15.2318 | 4 | 15.2318 | 70.1986 | 35.0993 | 15 | 35 | 0.099299 | -2.2191 | 0.0007888 | 1.9422e-05 | 1 | 0
744 | 12.4 | 4.9995 | 11.9992 | 5 | 12 | 70.2022 | 40 | 0.00075703 | 3.564 | -3.1776e-05 | 0.010531 | 4.8218 | 0 | 4.8324 |  | 15.2324 | 4 | 15.2324 | 70.2022 | 35.1011 | 15 | 35 | 0.10112 | -2.118 | 0.00075703 | 1.986e-05 | 1 | 0
745 | 12.4167 | 4.9995 | 11.9993 | 5 | 12 | 70.2055 | 40 | 0.0007246 | 3.5647 | -3.2424e-05 | 0.01008 | 4.8228 | 0 | 4.8329 |  | 15.2329 | 4 | 15.2329 | 70.2055 | 35.1028 | 15 | 35 | 0.10277 | -2.0152 | 0.0007246 | 2.0265e-05 | 1 | 0
746 | 12.4333 | 4.9996 | 11.9993 | 5 | 12 | 70.2085 | 40 | 0.00069159 | 3.5654 | -3.3018e-05 | 0.009621 | 4.8237 | 0 | 4.8334 |  | 15.2334 | 4 | 15.2334 | 70.2085 | 35.1043 | 15 | 35 | 0.10426 | -1.9109 | 0.00069159 | 2.0636e-05 | 1 | 0
747 | 12.45 | 4.9996 | 11.9993 | 5 | 12 | 70.2112 | 40 | 0.00065803 | 3.566 | -3.3558e-05 | 0.0091542 | 4.8246 | 0 | 4.8338 |  | 15.2338 | 4 | 15.2338 | 70.2112 | 35.1056 | 15 | 35 | 0.10558 | -1.8054 | 0.00065803 | 2.0974e-05 | 1 | 0
748 | 12.4667 | 4.9996 | 11.9994 | 5 | 12 | 70.2135 | 40 | 0.00062398 | 3.5667 | -3.4044e-05 | 0.0086806 | 4.8255 | 0 | 4.8342 |  | 15.2342 | 4 | 15.2342 | 70.2135 | 35.1067 | 15 | 35 | 0.10674 | -1.6986 | 0.00062398 | 2.1278e-05 | 1 | 0
749 | 12.4833 | 4.9996 | 11.9994 | 5 | 12 | 70.2155 | 40 | 0.00058951 | 3.5672 | -3.4476e-05 | 0.0082009 | 4.8263 | 0 | 4.8345 |  | 15.2345 | 4 | 15.2345 | 70.2155 | 35.1077 | 15 | 35 | 0.10774 | -1.5909 | 0.00058951 | 2.1548e-05 | 1 | 0
750 | 12.5 | 4.9997 | 11.9994 | 5 | 12 | 70.2171 | 40 | 0.00055465 | 3.5678 | -3.4855e-05 | 0.0077161 | 4.827 | 0 | 4.8347 |  | 15.2347 | 4 | 15.2347 | 70.2171 | 35.1086 | 15 | 35 | 0.10857 | -1.4823 | 0.00055465 | 2.1784e-05 | 1 | 0
751 | 12.5167 | 4.9997 | 11.9995 | 5 | 12 | 70.2185 | 40 | 0.00051947 | 3.5683 | -3.5179e-05 | 0.0072267 | 4.8277 | 0 | 4.835 |  | 15.235 | 4 | 15.235 | 70.2185 | 35.1092 | 15 | 35 | 0.10923 | -1.3731 | 0.00051947 | 2.1987e-05 | 1 | 0
752 | 12.5333 | 4.9997 | 11.9995 | 5 | 12 | 70.2195 | 40 | 0.00048402 | 3.5688 | -3.545e-05 | 0.0067335 | 4.8284 | 0 | 4.8351 |  | 15.2351 | 4 | 15.2351 | 70.2195 | 35.1097 | 15 | 35 | 0.10974 | -1.2633 | 0.00048402 | 2.2156e-05 | 1 | 0
753 | 12.55 | 4.9997 | 11.9996 | 5 | 12 | 70.2202 | 40 | 0.00044835 | 3.5693 | -3.5668e-05 | 0.0062373 | 4.829 | 0 | 4.8352 |  | 15.2352 | 4 | 15.2352 | 70.2202 | 35.1101 | 15 | 35 | 0.11008 | -1.1533 | 0.00044835 | 2.2292e-05 | 1 | 0
754 | 12.5667 | 4.9997 | 11.9996 | 5 | 12 | 70.2205 | 40 | 0.00041252 | 3.5697 | -3.5833e-05 | 0.0057388 | 4.8295 | 0 | 4.8353 |  | 15.2353 | 4 | 15.2353 | 70.2205 | 35.1103 | 15 | 35 | 0.11027 | -1.043 | 0.00041252 | 2.2395e-05 | 1 | 0
755 | 12.5833 | 4.9998 | 11.9996 | 5 | 12 | 70.2206 | 40 | 0.00037658 | 3.57 | -3.5945e-05 | 0.0052388 | 4.8301 | 0 | 4.8353 |  | 15.2353 | 4 | 15.2353 | 70.2206 | 35.1103 | 15 | 35 | 0.1103 | -0.9327 | 0.00037658 | 2.2466e-05 | 1 | 0
756 | 12.6 | 4.9998 | 11.9997 | 5 | 12 | 70.2203 | 40 | 0.00034057 | 3.5704 | -3.6006e-05 | 0.0047379 | 4.8305 | 0 | 4.8353 |  | 15.2353 | 4 | 15.2353 | 70.2203 | 35.1102 | 15 | 35 | 0.11017 | -0.82252 | 0.00034057 | 2.2504e-05 | 1 | 0
757 | 12.6167 | 4.9998 | 11.9997 | 5 | 12 | 70.2198 | 40 | 0.00030455 | 3.5707 | -3.6016e-05 | 0.0042368 | 4.8309 | 0 | 4.8352 |  | 15.2352 | 4 | 15.2352 | 70.2198 | 35.1099 | 15 | 35 | 0.1099 | -0.71263 | 0.00030455 | 2.251e-05 | 1 | 0
758 | 12.6333 | 4.9998 | 11.9997 | 5 | 12 | 70.2189 | 40 | 0.00026858 | 3.571 | -3.5975e-05 | 0.0037364 | 4.8313 | 0 | 4.835 |  | 15.235 | 4 | 15.235 | 70.2189 | 35.1095 | 15 | 35 | 0.10947 | -0.60316 | 0.00026858 | 2.2484e-05 | 1 | 0
759 | 12.65 | 4.9999 | 11.9998 | 5 | 12 | 70.2178 | 40 | 0.0002327 | 3.5712 | -3.5884e-05 | 0.0032372 | 4.8316 | 0 | 4.8348 |  | 15.2348 | 4 | 15.2348 | 70.2178 | 35.1089 | 15 | 35 | 0.10889 | -0.49427 | 0.0002327 | 2.2428e-05 | 1 | 0
760 | 12.6667 | 4.9999 | 11.9998 | 5 | 12 | 70.2163 | 40 | 0.00019695 | 3.5714 | -3.5744e-05 | 0.0027399 | 4.8319 | 0 | 4.8346 |  | 15.2346 | 4 | 15.2346 | 70.2163 | 35.1082 | 15 | 35 | 0.10817 | -0.3861 | 0.00019695 | 2.234e-05 | 1 | 0
761 | 12.6833 | 4.9999 | 11.9998 | 5 | 12 | 70.2146 | 40 | 0.00016139 | 3.5715 | -3.5556e-05 | 0.0022453 | 4.8321 | 0 | 4.8343 |  | 15.2343 | 4 | 15.2343 | 70.2146 | 35.1073 | 15 | 35 | 0.10731 | -0.2788 | 0.00016139 | 2.2223e-05 | 1 | 0
762 | 12.7 | 4.9999 | 11.9999 | 5 | 12 | 70.2126 | 40 | 0.00012607 | 3.5717 | -3.5321e-05 | 0.0017539 | 4.8323 | 0 | 4.834 |  | 15.234 | 4 | 15.234 | 70.2126 | 35.1063 | 15 | 35 | 0.1063 | -0.17249 | 0.00012607 | 2.2075e-05 | 1 | 0
763 | 12.7167 | 4.9999 | 11.9999 | 5 | 12 | 70.2103 | 40 | 9.1036e-05 | 3.5718 | -3.5039e-05 | 0.0012664 | 4.8324 | 0 | 4.8337 |  | 15.2337 | 4 | 15.2337 | 70.2103 | 35.1052 | 15 | 35 | 0.10517 | -0.067328 | 9.1036e-05 | 2.1899e-05 | 1 | 0
764 | 12.7333 | 5 | 11.9999 | 5 | 12 | 70.2078 | 40 | 5.6324e-05 | 3.5718 | -3.4711e-05 | 0.00078356 | 4.8325 | 0 | 4.8332 |  | 15.2332 | 4 | 15.2332 | 70.2078 | 35.1039 | 15 | 35 | 0.10389 | 0.036566 | 5.6324e-05 | 2.1695e-05 | 1 | 0
765 | 12.75 | 5 | 12 | 5 | 12 | 70.205 | 40 | 2.1985e-05 | 3.5718 | -3.434e-05 | 0.00030584 | 4.8325 | 0 | 4.8328 |  | 15.2328 | 4 | 15.2328 | 70.205 | 35.1025 | 15 | 35 | 0.10249 | 0.13906 | 2.1985e-05 | 2.1462e-05 | 1 | 0
766 | 12.7667 | 5 | 12 | 5 | 12 | 70.2019 | 40 | -1.194e-05 | 3.5718 | -3.3925e-05 | -0.0001661 | 4.8325 | 0 | 4.8323 |  | 15.2323 | 4 | 15.2323 | 70.2019 | 35.101 | 15 | 35 | 0.10097 | 0.24003 | 1.194e-05 | 2.1203e-05 | 1 | 0
767 | 12.7833 | 5 | 12 | 5 | 12 | 70.1986 | 40 | -4.5408e-05 | 3.5718 | -3.3468e-05 | -0.00063169 | 4.8324 | 0 | 4.8318 |  | 15.2318 | 4 | 15.2318 | 70.1986 | 35.0993 | 15 | 35 | 0.099322 | 0.33935 | 4.5408e-05 | 2.0917e-05 | 1 | 0
768 | 12.8 | 5 | 12.0001 | 5 | 12 | 70.1951 | 40 | -7.8377e-05 | 3.5717 | -3.2969e-05 | -0.0010903 | 4.8323 | 0 | 4.8312 |  | 15.2312 | 4 | 15.2312 | 70.1951 | 35.0976 | 15 | 35 | 0.097557 | 0.43691 | 7.8377e-05 | 2.0606e-05 | 1 | 0
769 | 12.8167 | 5.0001 | 12.0001 | 5 | 12 | 70.1914 | 40 | -0.00011081 | 3.5716 | -3.2432e-05 | -0.0015415 | 4.8322 | 0 | 4.8306 |  | 15.2306 | 4 | 15.2306 | 70.1914 | 35.0957 | 15 | 35 | 0.095679 | 0.53259 | 0.00011081 | 2.027e-05 | 1 | 0
770 | 12.8333 | 5.0001 | 12.0001 | 5 | 12 | 70.1874 | 40 | -0.00014266 | 3.5715 | -3.1855e-05 | -0.0019847 | 4.832 | 0 | 4.83 |  | 15.23 | 4 | 15.23 | 70.1874 | 35.0937 | 15 | 35 | 0.093691 | 0.62628 | 0.00014266 | 1.991e-05 | 1 | 0
771 | 12.85 | 5.0001 | 12.0002 | 5 | 12 | 70.1832 | 40 | -0.00017391 | 3.5713 | -3.1242e-05 | -0.0024193 | 4.8317 | 0 | 4.8293 |  | 15.2293 | 4 | 15.2293 | 70.1832 | 35.0916 | 15 | 35 | 0.091597 | 0.71788 | 0.00017391 | 1.9526e-05 | 1 | 0
772 | 12.8667 | 5.0001 | 12.0002 | 5 | 12 | 70.1788 | 40 | -0.0002045 | 3.5711 | -3.0593e-05 | -0.0028449 | 4.8315 | 0 | 4.8286 |  | 15.2286 | 4 | 15.2286 | 70.1788 | 35.0894 | 15 | 35 | 0.089403 | 0.80728 | 0.0002045 | 1.9121e-05 | 1 | 0
773 | 12.8833 | 5.0001 | 12.0002 | 5 | 12 | 70.1742 | 40 | -0.00023441 | 3.5708 | -2.9909e-05 | -0.003261 | 4.8311 | 0 | 4.8279 |  | 15.2279 | 4 | 15.2279 | 70.1742 | 35.0871 | 15 | 35 | 0.087111 | 0.89439 | 0.00023441 | 1.8693e-05 | 1 | 0
774 | 12.9 | 5.0002 | 12.0003 | 5 | 12 | 70.1695 | 40 | -0.0002636 | 3.5706 | -2.9193e-05 | -0.0036671 | 4.8308 | 0 | 4.8271 |  | 15.2271 | 4 | 15.2271 | 70.1695 | 35.0847 | 15 | 35 | 0.084728 | 0.97912 | 0.0002636 | 1.8245e-05 | 1 | 0
775 | 12.9167 | 5.0002 | 12.0003 | 5 | 12 | 70.1645 | 40 | -0.00029205 | 3.5703 | -2.8445e-05 | -0.0040628 | 4.8304 | 0 | 4.8263 |  | 15.2263 | 4 | 15.2263 | 70.1645 | 35.0823 | 15 | 35 | 0.082257 | 1.0614 | 0.00029205 | 1.7778e-05 | 1 | 0
776 | 12.9333 | 5.0002 | 12.0003 | 5 | 12 | 70.1594 | 40 | -0.00031971 | 3.57 | -2.7666e-05 | -0.0044477 | 4.83 | 0 | 4.8255 |  | 15.2255 | 4 | 15.2255 | 70.1594 | 35.0797 | 15 | 35 | 0.079702 | 1.1411 | 0.00031971 | 1.7291e-05 | 1 | 0
777 | 12.95 | 5.0002 | 12.0003 | 5 | 12 | 70.1541 | 40 | -0.00034657 | 3.5696 | -2.6859e-05 | -0.0048213 | 4.8295 | 0 | 4.8247 |  | 15.2247 | 4 | 15.2247 | 70.1541 | 35.0771 | 15 | 35 | 0.077069 | 1.2181 | 0.00034657 | 1.6787e-05 | 1 | 0
778 | 12.9667 | 5.0002 | 12.0004 | 5 | 12 | 70.1487 | 40 | -0.0003726 | 3.5692 | -2.6025e-05 | -0.0051834 | 4.829 | 0 | 4.8238 |  | 15.2238 | 4 | 15.2238 | 70.1487 | 35.0744 | 15 | 35 | 0.074362 | 1.2925 | 0.0003726 | 1.6266e-05 | 1 | 0
779 | 12.9833 | 5.0002 | 12.0004 | 5 | 12 | 70.1432 | 40 | -0.00039776 | 3.5688 | -2.5165e-05 | -0.0055335 | 4.8284 | 0 | 4.8229 |  | 15.2229 | 4 | 15.2229 | 70.1432 | 35.0716 | 15 | 35 | 0.071587 | 1.3641 | 0.00039776 | 1.5728e-05 | 1 | 0
780 | 13 | 5.0003 | 12.0004 | 5 | 12 | 70.1375 | 40 | -0.00042204 | 3.5684 | -2.4282e-05 | -0.0058713 | 4.8279 | 0 | 4.822 |  | 15.222 | 4 | 15.222 | 70.1375 | 35.0687 | 15 | 35 | 0.068747 | 1.4328 | 0.00042204 | 1.5176e-05 | 1 | 0
781 | 13.0167 | 5.0003 | 12.0004 | 5 | 12 | 70.1317 | 40 | -0.00044542 | 3.568 | -2.3375e-05 | -0.0061965 | 4.8273 | 0 | 4.8211 |  | 15.2211 | 4 | 15.2211 | 70.1317 | 35.0658 | 15 | 35 | 0.065847 | 1.4987 | 0.00044542 | 1.461e-05 | 1 | 0
782 | 13.0333 | 5.0003 | 12.0005 | 5 | 12 | 70.1258 | 40 | -0.00046787 | 3.5675 | -2.2448e-05 | -0.0065088 | 4.8266 | 0 | 4.8201 |  | 15.2201 | 4 | 15.2201 | 70.1258 | 35.0629 | 15 | 35 | 0.062893 | 1.5616 | 0.00046787 | 1.403e-05 | 1 | 0
783 | 13.05 | 5.0003 | 12.0005 | 5 | 12 | 70.1198 | 40 | -0.00048937 | 3.567 | -2.1501e-05 | -0.0068079 | 4.826 | 0 | 4.8192 |  | 15.2192 | 4 | 15.2192 | 70.1198 | 35.0599 | 15 | 35 | 0.059889 | 1.6215 | 0.00048937 | 1.3438e-05 | 1 | 0
784 | 13.0667 | 5.0003 | 12.0005 | 5 | 12 | 70.1137 | 40 | -0.0005099 | 3.5665 | -2.0537e-05 | -0.0070936 | 4.8253 | 0 | 4.8182 |  | 15.2182 | 4 | 15.2182 | 70.1137 | 35.0568 | 15 | 35 | 0.056841 | 1.6783 | 0.0005099 | 1.2835e-05 | 1 | 0
785 | 13.0833 | 5.0003 | 12.0005 | 5 | 12 | 70.1075 | 40 | -0.00052946 | 3.566 | -1.9556e-05 | -0.0073656 | 4.8246 | 0 | 4.8172 |  | 15.2172 | 4 | 15.2172 | 70.1075 | 35.0538 | 15 | 35 | 0.053752 | 1.7321 | 0.00052946 | 1.2222e-05 | 1 | 0
786 | 13.1 | 5.0003 | 12.0005 | 5 | 12 | 70.1013 | 40 | -0.00054802 | 3.5654 | -1.856e-05 | -0.0076238 | 4.8238 | 0 | 4.8162 |  | 15.2162 | 4 | 15.2162 | 70.1013 | 35.0506 | 15 | 35 | 0.050628 | 1.7827 | 0.00054802 | 1.16e-05 | 1 | 0
787 | 13.1167 | 5.0004 | 12.0006 | 5 | 12 | 70.0949 | 40 | -0.00056557 | 3.5649 | -1.7552e-05 | -0.007868 | 4.8231 | 0 | 4.8152 |  | 15.2152 | 4 | 15.2152 | 70.0949 | 35.0475 | 15 | 35 | 0.047474 | 1.8302 | 0.00056557 | 1.097e-05 | 1 | 0
788 | 13.1333 | 5.0004 | 12.0006 | 5 | 12 | 70.0886 | 40 | -0.0005821 | 3.5643 | -1.6532e-05 | -0.008098 | 4.8223 | 0 | 4.8142 |  | 15.2142 | 4 | 15.2142 | 70.0886 | 35.0443 | 15 | 35 | 0.044294 | 1.8745 | 0.0005821 | 1.0332e-05 | 1 | 0
789 | 13.15 | 5.0004 | 12.0006 | 5 | 12 | 70.0822 | 40 | -0.00059761 | 3.5637 | -1.5502e-05 | -0.0083136 | 4.8215 | 0 | 4.8131 |  | 15.2131 | 4 | 15.2131 | 70.0822 | 35.0411 | 15 | 35 | 0.041094 | 1.9156 | 0.00059761 | 9.6886e-06 | 1 | 0
790 | 13.1667 | 5.0004 | 12.0006 | 5 | 12 | 70.0758 | 40 | -0.00061207 | 3.5631 | -1.4463e-05 | -0.0085148 | 4.8206 | 0 | 4.8121 |  | 15.2121 | 4 | 15.2121 | 70.0758 | 35.0379 | 15 | 35 | 0.037877 | 1.9534 | 0.00061207 | 9.0396e-06 | 1 | 0
791 | 13.1833 | 5.0004 | 12.0006 | 5 | 12 | 70.0693 | 40 | -0.00062549 | 3.5625 | -1.3418e-05 | -0.0087015 | 4.8198 | 0 | 4.8111 |  | 15.2111 | 4 | 15.2111 | 70.0693 | 35.0346 | 15 | 35 | 0.034649 | 1.9881 | 0.00062549 | 8.3865e-06 | 1 | 0
792 | 13.2 | 5.0004 | 12.0006 | 5 | 12 | 70.0628 | 40 | -0.00063786 | 3.5618 | -1.2368e-05 | -0.0088736 | 4.8189 | 0 | 4.8101 |  | 15.2101 | 4 | 15.2101 | 70.0628 | 35.0314 | 15 | 35 | 0.031415 | 2.0195 | 0.00063786 | 7.73e-06 | 1 | 0
793 | 13.2167 | 5.0004 | 12.0006 | 5 | 12 | 70.0564 | 40 | -0.00064917 | 3.5612 | -1.1314e-05 | -0.009031 | 4.818 | 0 | 4.809 |  | 15.209 | 4 | 15.209 | 70.0564 | 35.0282 | 15 | 35 | 0.028178 | 2.0477 | 0.00064917 | 7.0713e-06 | 1 | 0
794 | 13.2333 | 5.0004 | 12.0007 | 5 | 12 | 70.0499 | 40 | -0.00065943 | 3.5605 | -1.0258e-05 | -0.0091737 | 4.8172 | 0 | 4.808 |  | 15.208 | 4 | 15.208 | 70.0499 | 35.0249 | 15 | 35 | 0.024944 | 2.0726 | 0.00065943 | 6.4112e-06 | 1 | 0
795 | 13.25 | 5.0004 | 12.0007 | 5 | 12 | 70.0434 | 40 | -0.00066863 | 3.5598 | -9.2011e-06 | -0.0093017 | 4.8163 | 0 | 4.8069 |  | 15.2069 | 4 | 15.2069 | 70.0434 | 35.0217 | 15 | 35 | 0.021717 | 2.0943 | 0.00066863 | 5.7507e-06 | 1 | 0
796 | 13.2667 | 5.0004 | 12.0007 | 5 | 12 | 70.037 | 40 | -0.00067677 | 3.5592 | -8.1451e-06 | -0.009415 | 4.8153 | 0 | 4.8059 |  | 15.2059 | 4 | 15.2059 | 70.037 | 35.0185 | 15 | 35 | 0.018502 | 2.1128 | 0.00067677 | 5.0907e-06 | 1 | 0
797 | 13.2833 | 5.0004 | 12.0007 | 5 | 12 | 70.0306 | 40 | -0.00068386 | 3.5585 | -7.0914e-06 | -0.0095136 | 4.8144 | 0 | 4.8049 |  | 15.2049 | 4 | 15.2049 | 70.0306 | 35.0153 | 15 | 35 | 0.015302 | 2.1281 | 0.00068386 | 4.4321e-06 | 1 | 0
798 | 13.3 | 5.0004 | 12.0007 | 5 | 12 | 70.0242 | 40 | -0.00068991 | 3.5578 | -6.0414e-06 | -0.0095977 | 4.8135 | 0 | 4.8039 |  | 15.2039 | 4 | 15.2039 | 70.0242 | 35.0121 | 15 | 35 | 0.012123 | 2.1403 | 0.00068991 | 3.7759e-06 | 1 | 0
799 | 13.3167 | 5.0004 | 12.0007 | 5 | 12 | 70.0179 | 40 | -0.0006949 | 3.5571 | -4.9967e-06 | -0.0096672 | 4.8125 | 0 | 4.8029 |  | 15.2029 | 4 | 15.2029 | 70.0179 | 35.009 | 15 | 35 | 0.0089675 | 2.1492 | 0.0006949 | 3.1229e-06 | 1 | 0
800 | 13.3333 | 5.0004 | 12.0007 | 5 | 12 | 70.0117 | 40 | -0.00069886 | 3.5564 | -3.9584e-06 | -0.0097222 | 4.8116 | 0 | 4.8019 |  | 15.2019 | 4 | 15.2019 | 70.0117 | 35.0058 | 15 | 35 | 0.0058407 | 2.1551 | 0.00069886 | 2.474e-06 | 1 | 0
801 | 13.35 | 5.0004 | 12.0007 | 5 | 12 | 70.0055 | 40 | -0.00070179 | 3.5557 | -2.9282e-06 | -0.009763 | 4.8106 | 0 | 4.8009 |  | 15.2009 | 4 | 15.2009 | 70.0055 | 35.0027 | 15 | 35 | 0.0027463 | 2.1578 | 0.00070179 | 1.8301e-06 | 1 | 0
802 | 13.3667 | 5.0004 | 12.0007 | 5 | 12 | 69.9994 | 40 | -0.0007037 | 3.555 | -1.9072e-06 | -0.0097895 | 4.8097 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9994 | 34.9997 | 15 | 35 | -0.00031184 | 2.1575 | 0.0007037 | 1.192e-06 | 1 | 0
803 | 13.3833 | 5.0004 | 12.0007 | 5 | 12 | 69.9933 | 40 | -0.00070459 | 3.5543 | -8.9674e-07 | -0.009802 | 4.8087 | 0 | 4.7989 |  | 15.1989 | 4 | 15.1989 | 69.9933 | 34.9967 | 15 | 35 | -0.0033298 | 2.1542 | 0.00070459 | 5.6046e-07 | 1 | 0
804 | 13.4 | 5.0004 | 12.0007 | 5 | 12 | 69.9874 | 40 | -0.00070449 | 3.5536 | 1.0183e-07 | -0.0098006 | 4.8078 | 0 | 4.798 |  | 15.198 | 4 | 15.198 | 69.9874 | 34.9937 | 15 | 35 | -0.0063039 | 2.1479 | 0.00070449 | -6.3642e-08 | -1 | -2
805 | 13.4167 | 5.0004 | 12.0007 | 5 | 12 | 69.9815 | 40 | -0.0007034 | 3.5529 | 1.0873e-06 | -0.0097854 | 4.8068 | 0 | 4.797 |  | 15.197 | 4 | 15.197 | 69.9815 | 34.9908 | 15 | 35 | -0.0092306 | 2.1386 | 0.0007034 | -6.7955e-07 | -1 | 0
806 | 13.4333 | 5.0004 | 12.0007 | 5 | 12 | 69.9758 | 40 | -0.00070135 | 3.5522 | 2.0584e-06 | -0.0097568 | 4.8059 | 0 | 4.7961 |  | 15.1961 | 4 | 15.1961 | 69.9758 | 34.9879 | 15 | 35 | -0.012106 | 2.1265 | 0.00070135 | -1.2865e-06 | -1 | 0
807 | 13.45 | 5.0004 | 12.0007 | 5 | 12 | 69.9701 | 40 | -0.00069833 | 3.5515 | 3.0141e-06 | -0.0097149 | 4.8049 | 0 | 4.7952 |  | 15.1952 | 4 | 15.1952 | 69.9701 | 34.9851 | 15 | 35 | -0.014928 | 2.1116 | 0.00069833 | -1.8838e-06 | -1 | 0
808 | 13.4667 | 5.0004 | 12.0007 | 5 | 12 | 69.9646 | 40 | -0.00069438 | 3.5508 | 3.9531e-06 | -0.0096599 | 4.804 | 0 | 4.7943 |  | 15.1943 | 4 | 15.1943 | 69.9646 | 34.9823 | 15 | 35 | -0.017692 | 2.0939 | 0.00069438 | -2.4707e-06 | -1 | 0
809 | 13.4833 | 5.0004 | 12.0007 | 5 | 12 | 69.9592 | 40 | -0.0006895 | 3.5501 | 4.8744e-06 | -0.0095921 | 4.8031 | 0 | 4.7935 |  | 15.1935 | 4 | 15.1935 | 69.9592 | 34.9796 | 15 | 35 | -0.020395 | 2.0735 | 0.0006895 | -3.0465e-06 | -1 | 0
810 | 13.5 | 5.0004 | 12.0007 | 5 | 12 | 69.9539 | 40 | -0.00068373 | 3.5494 | 5.7769e-06 | -0.0095117 | 4.8021 | 0 | 4.7926 |  | 15.1926 | 4 | 15.1926 | 69.9539 | 34.977 | 15 | 35 | -0.023035 | 2.0505 | 0.00068373 | -3.6106e-06 | -1 | 0
811 | 13.5167 | 5.0004 | 12.0007 | 5 | 12 | 69.9488 | 40 | -0.00067707 | 3.5487 | 6.6596e-06 | -0.0094191 | 4.8012 | 0 | 4.7918 |  | 15.1918 | 4 | 15.1918 | 69.9488 | 34.9744 | 15 | 35 | -0.025608 | 2.0249 | 0.00067707 | -4.1623e-06 | -1 | 0
812 | 13.5333 | 5.0004 | 12.0007 | 5 | 12 | 69.9438 | 40 | -0.00066955 | 3.5481 | 7.5215e-06 | -0.0093144 | 4.8003 | 0 | 4.791 |  | 15.191 | 4 | 15.191 | 69.9438 | 34.9719 | 15 | 35 | -0.028112 | 1.9968 | 0.00066955 | -4.701e-06 | -1 | 0
813 | 13.55 | 5.0004 | 12.0007 | 5 | 12 | 69.9389 | 40 | -0.00066118 | 3.5474 | 8.3617e-06 | -0.0091981 | 4.7994 | 0 | 4.7902 |  | 15.1902 | 4 | 15.1902 | 69.9389 | 34.9695 | 15 | 35 | -0.030544 | 1.9662 | 0.00066118 | -5.2261e-06 | -1 | 0
814 | 13.5667 | 5.0004 | 12.0007 | 5 | 12 | 69.9342 | 40 | -0.00065201 | 3.5467 | 9.1793e-06 | -0.0090704 | 4.7985 | 0 | 4.7895 |  | 15.1895 | 4 | 15.1895 | 69.9342 | 34.9671 | 15 | 35 | -0.032901 | 1.9333 | 0.00065201 | -5.7371e-06 | -1 | 0
815 | 13.5833 | 5.0004 | 12.0006 | 5 | 12 | 69.9296 | 40 | -0.00064203 | 3.5461 | 9.9734e-06 | -0.0089317 | 4.7977 | 0 | 4.7887 |  | 15.1887 | 4 | 15.1887 | 69.9296 | 34.9648 | 15 | 35 | -0.035182 | 1.8981 | 0.00064203 | -6.2334e-06 | -1 | 0
816 | 13.6 | 5.0004 | 12.0006 | 5 | 12 | 69.9252 | 40 | -0.00063129 | 3.5455 | 1.0743e-05 | -0.0087822 | 4.7968 | 0 | 4.788 |  | 15.188 | 4 | 15.188 | 69.9252 | 34.9626 | 15 | 35 | -0.037384 | 1.8608 | 0.00063129 | -6.7145e-06 | -1 | 0
817 | 13.6167 | 5.0004 | 12.0006 | 5 | 12 | 69.921 | 40 | -0.0006198 | 3.5449 | 1.1488e-05 | -0.0086224 | 4.796 | 0 | 4.7874 |  | 15.1874 | 4 | 15.1874 | 69.921 | 34.9605 | 15 | 35 | -0.039505 | 1.8212 | 0.0006198 | -7.18e-06 | -1 | 0
818 | 13.6333 | 5.0004 | 12.0006 | 5 | 12 | 69.9169 | 40 | -0.00060759 | 3.5442 | 1.2207e-05 | -0.0084526 | 4.7952 | 0 | 4.7867 |  | 15.1867 | 4 | 15.1867 | 69.9169 | 34.9585 | 15 | 35 | -0.041543 | 1.7797 | 0.00060759 | -7.6294e-06 | -1 | 0
819 | 13.65 | 5.0004 | 12.0006 | 5 | 12 | 69.913 | 40 | -0.00059469 | 3.5437 | 1.29e-05 | -0.0082731 | 4.7944 | 0 | 4.7861 |  | 15.1861 | 4 | 15.1861 | 69.913 | 34.9565 | 15 | 35 | -0.043497 | 1.7362 | 0.00059469 | -8.0623e-06 | -1 | 0
820 | 13.6667 | 5.0004 | 12.0006 | 5 | 12 | 69.9093 | 40 | -0.00058113 | 3.5431 | 1.3565e-05 | -0.0080844 | 4.7936 | 0 | 4.7855 |  | 15.1855 | 4 | 15.1855 | 69.9093 | 34.9546 | 15 | 35 | -0.045364 | 1.6908 | 0.00058113 | -8.4782e-06 | -1 | 0
821 | 13.6833 | 5.0004 | 12.0006 | 5 | 12 | 69.9057 | 40 | -0.00056693 | 3.5425 | 1.4203e-05 | -0.0078868 | 4.7928 | 0 | 4.7849 |  | 15.1849 | 4 | 15.1849 | 69.9057 | 34.9529 | 15 | 35 | -0.047143 | 1.6437 | 0.00056693 | -8.8769e-06 | -1 | 0
822 | 13.7 | 5.0003 | 12.0006 | 5 | 12 | 69.9023 | 40 | -0.00055211 | 3.542 | 1.4813e-05 | -0.0076808 | 4.7921 | 0 | 4.7844 |  | 15.1844 | 4 | 15.1844 | 69.9023 | 34.9512 | 15 | 35 | -0.048834 | 1.5949 | 0.00055211 | -9.258e-06 | -1 | 0
823 | 13.7167 | 5.0003 | 12.0005 | 5 | 12 | 69.8991 | 40 | -0.00053672 | 3.5414 | 1.5394e-05 | -0.0074666 | 4.7913 | 0 | 4.7839 |  | 15.1839 | 4 | 15.1839 | 69.8991 | 34.9496 | 15 | 35 | -0.050434 | 1.5444 | 0.00053672 | -9.6211e-06 | -1 | 0
824 | 13.7333 | 5.0003 | 12.0005 | 5 | 12 | 69.8961 | 40 | -0.00052077 | 3.5409 | 1.5946e-05 | -0.0072448 | 4.7906 | 0 | 4.7834 |  | 15.1834 | 4 | 15.1834 | 69.8961 | 34.9481 | 15 | 35 | -0.051942 | 1.4925 | 0.00052077 | -9.9661e-06 | -1 | 0
825 | 13.75 | 5.0003 | 12.0005 | 5 | 12 | 69.8933 | 40 | -0.00050431 | 3.5404 | 1.6468e-05 | -0.0070157 | 4.7899 | 0 | 4.7829 |  | 15.1829 | 4 | 15.1829 | 69.8933 | 34.9466 | 15 | 35 | -0.053359 | 1.4391 | 0.00050431 | -1.0293e-05 | -1 | 0
826 | 13.7667 | 5.0003 | 12.0005 | 5 | 12 | 69.8906 | 40 | -0.00048734 | 3.5399 | 1.6961e-05 | -0.0067797 | 4.7893 | 0 | 4.7825 |  | 15.1825 | 4 | 15.1825 | 69.8906 | 34.9453 | 15 | 35 | -0.054682 | 1.3845 | 0.00048734 | -1.06e-05 | -1 | 0
827 | 13.7833 | 5.0003 | 12.0005 | 5 | 12 | 69.8882 | 40 | -0.00046992 | 3.5394 | 1.7423e-05 | -0.0065373 | 4.7886 | 0 | 4.7821 |  | 15.1821 | 4 | 15.1821 | 69.8882 | 34.9441 | 15 | 35 | -0.055911 | 1.3285 | 0.00046992 | -1.089e-05 | -1 | 0
828 | 13.8 | 5.0003 | 12.0005 | 5 | 12 | 69.8859 | 40 | -0.00045207 | 3.539 | 1.7855e-05 | -0.0062889 | 4.788 | 0 | 4.7817 |  | 15.1817 | 4 | 15.1817 | 69.8859 | 34.943 | 15 | 35 | -0.057046 | 1.2715 | 0.00045207 | -1.116e-05 | -1 | 0
829 | 13.8167 | 5.0003 | 12.0004 | 5 | 12 | 69.8838 | 40 | -0.00043381 | 3.5385 | 1.8257e-05 | -0.006035 | 4.7874 | 0 | 4.7814 |  | 15.1814 | 4 | 15.1814 | 69.8838 | 34.9419 | 15 | 35 | -0.058087 | 1.2134 | 0.00043381 | -1.141e-05 | -1 | 0
830 | 13.8333 | 5.0003 | 12.0004 | 5 | 12 | 69.8819 | 40 | -0.00041518 | 3.5381 | 1.8627e-05 | -0.0057758 | 4.7869 | 0 | 4.7811 |  | 15.1811 | 4 | 15.1811 | 69.8819 | 34.941 | 15 | 35 | -0.059032 | 1.1544 | 0.00041518 | -1.1642e-05 | -1 | 0
831 | 13.85 | 5.0002 | 12.0004 | 5 | 12 | 69.8802 | 40 | -0.00039621 | 3.5377 | 1.8967e-05 | -0.005512 | 4.7863 | 0 | 4.7808 |  | 15.1808 | 4 | 15.1808 | 69.8802 | 34.9401 | 15 | 35 | -0.059883 | 1.0945 | 0.00039621 | -1.1854e-05 | -1 | 0
832 | 13.8667 | 5.0002 | 12.0004 | 5 | 12 | 69.8787 | 40 | -0.00037694 | 3.5374 | 1.9276e-05 | -0.0052438 | 4.7858 | 0 | 4.7806 |  | 15.1806 | 4 | 15.1806 | 69.8787 | 34.9394 | 15 | 35 | -0.060638 | 1.0339 | 0.00037694 | -1.2047e-05 | -1 | 0
833 | 13.8833 | 5.0002 | 12.0004 | 5 | 12 | 69.8774 | 40 | -0.00035739 | 3.537 | 1.9554e-05 | -0.0049718 | 4.7854 | 0 | 4.7804 |  | 15.1804 | 4 | 15.1804 | 69.8774 | 34.9387 | 15 | 35 | -0.061299 | 0.97256 | 0.00035739 | -1.2221e-05 | -1 | 0
834 | 13.9 | 5.0002 | 12.0003 | 5 | 12 | 69.8763 | 40 | -0.00033759 | 3.5367 | 1.98e-05 | -0.0046963 | 4.7849 | 0 | 4.7802 |  | 15.1802 | 4 | 15.1802 | 69.8763 | 34.9381 | 15 | 35 | -0.061866 | 0.91069 | 0.00033759 | -1.2375e-05 | -1 | 0
835 | 13.9167 | 5.0002 | 12.0003 | 5 | 12 | 69.8753 | 40 | -0.00031757 | 3.5363 | 2.0016e-05 | -0.0044179 | 4.7845 | 0 | 4.7801 |  | 15.1801 | 4 | 15.1801 | 69.8753 | 34.9377 | 15 | 35 | -0.062338 | 0.84835 | 0.00031757 | -1.251e-05 | -1 | 0
836 | 13.9333 | 5.0002 | 12.0003 | 5 | 12 | 69.8746 | 40 | -0.00029737 | 3.536 | 2.0201e-05 | -0.0041369 | 4.7841 | 0 | 4.7799 |  | 15.1799 | 4 | 15.1799 | 69.8746 | 34.9373 | 15 | 35 | -0.062717 | 0.78563 | 0.00029737 | -1.2626e-05 | -1 | 0
837 | 13.95 | 5.0002 | 12.0003 | 5 | 12 | 69.874 | 40 | -0.00027701 | 3.5358 | 2.0355e-05 | -0.0038537 | 4.7837 | 0 | 4.7798 |  | 15.1798 | 4 | 15.1798 | 69.874 | 34.937 | 15 | 35 | -0.063004 | 0.72263 | 0.00027701 | -1.2722e-05 | -1 | 0
838 | 13.9667 | 5.0002 | 12.0003 | 5 | 12 | 69.8736 | 40 | -0.00025653 | 3.5355 | 2.0479e-05 | -0.0035688 | 4.7833 | 0 | 4.7798 |  | 15.1798 | 4 | 15.1798 | 69.8736 | 34.9368 | 15 | 35 | -0.063198 | 0.65943 | 0.00025653 | -1.2799e-05 | -1 | 0
839 | 13.9833 | 5.0001 | 12.0002 | 5 | 12 | 69.8734 | 40 | -0.00023596 | 3.5353 | 2.0573e-05 | -0.0032826 | 4.783 | 0 | 4.7797 |  | 15.1797 | 4 | 15.1797 | 69.8734 | 34.9367 | 15 | 35 | -0.063301 | 0.59613 | 0.00023596 | -1.2858e-05 | -1 | 0
840 | 14 | 5.0001 | 12.0002 | 5 | 12 | 69.8734 | 40 | -0.00021532 | 3.5351 | 2.0636e-05 | -0.0029955 | 4.7827 | 0 | 4.7797 |  | 15.1797 | 4 | 15.1797 | 69.8734 | 34.9367 | 15 | 35 | -0.063315 | 0.53282 | 0.00021532 | -1.2898e-05 | -1 | 0
841 | 14.0167 | 5.0001 | 12.0002 | 5 | 12 | 69.8735 | 40 | -0.00019465 | 3.5349 | 2.067e-05 | -0.002708 | 4.7825 | 0 | 4.7798 |  | 15.1798 | 4 | 15.1798 | 69.8735 | 34.9368 | 15 | 35 | -0.063239 | 0.46958 | 0.00019465 | -1.2919e-05 | -1 | 0
842 | 14.0333 | 5.0001 | 12.0002 | 5 | 12 | 69.8738 | 40 | -0.00017398 | 3.5347 | 2.0674e-05 | -0.0024203 | 4.7822 | 0 | 4.7798 |  | 15.1798 | 4 | 15.1798 | 69.8738 | 34.9369 | 15 | 35 | -0.063076 | 0.4065 | 0.00017398 | -1.2921e-05 | -1 | 0
843 | 14.05 | 5.0001 | 12.0002 | 5 | 12 | 69.8743 | 40 | -0.00015333 | 3.5345 | 2.0649e-05 | -0.0021331 | 4.782 | 0 | 4.7799 |  | 15.1799 | 4 | 15.1799 | 69.8743 | 34.9372 | 15 | 35 | -0.062826 | 0.34367 | 0.00015333 | -1.2906e-05 | -1 | 0
844 | 14.0667 | 5.0001 | 12.0001 | 5 | 12 | 69.875 | 40 | -0.00013274 | 3.5344 | 2.0596e-05 | -0.0018466 | 4.7818 | 0 | 4.78 |  | 15.18 | 4 | 15.18 | 69.875 | 34.9375 | 15 | 35 | -0.062492 | 0.28118 | 0.00013274 | -1.2873e-05 | -1 | 0
845 | 14.0833 | 5.0001 | 12.0001 | 5 | 12 | 69.8759 | 40 | -0.00011222 | 3.5343 | 2.0515e-05 | -0.0015612 | 4.7817 | 0 | 4.7801 |  | 15.1801 | 4 | 15.1801 | 69.8759 | 34.9379 | 15 | 35 | -0.062075 | 0.21911 | 0.00011222 | -1.2822e-05 | -1 | 0
846 | 14.1 | 5.0001 | 12.0001 | 5 | 12 | 69.8768 | 40 | -9.1815e-05 | 3.5342 | 2.0406e-05 | -0.0012773 | 4.7816 | 0 | 4.7803 |  | 15.1803 | 4 | 15.1803 | 69.8768 | 34.9384 | 15 | 35 | -0.061576 | 0.15753 | 9.1815e-05 | -1.2753e-05 | -1 | 0
847 | 14.1167 | 5 | 12.0001 | 5 | 12 | 69.878 | 40 | -7.1545e-05 | 3.5341 | 2.0269e-05 | -0.00099531 | 4.7815 | 0 | 4.7805 |  | 15.1805 | 4 | 15.1805 | 69.878 | 34.939 | 15 | 35 | -0.060997 | 0.096535 | 7.1545e-05 | -1.2668e-05 | -1 | 0
848 | 14.1333 | 5 | 12.0001 | 5 | 12 | 69.8793 | 40 | -5.1439e-05 | 3.5341 | 2.0106e-05 | -0.0007156 | 4.7814 | 0 | 4.7807 |  | 15.1807 | 4 | 15.1807 | 69.8793 | 34.9397 | 15 | 35 | -0.06034 | 0.036195 | 5.1439e-05 | -1.2566e-05 | -1 | 0
849 | 14.15 | 5 | 12 | 5 | 12 | 69.8808 | 40 | -3.1522e-05 | 3.5341 | 1.9917e-05 | -0.00043852 | 4.7814 | 0 | 4.7809 |  | 15.1809 | 4 | 15.1809 | 69.8808 | 34.9404 | 15 | 35 | -0.059608 | -0.023413 | 3.1522e-05 | -1.2448e-05 | -1 | 0
850 | 14.1667 | 5 | 12 | 5 | 12 | 69.8824 | 40 | -1.1819e-05 | 3.534 | 1.9703e-05 | -0.00016442 | 4.7813 | 0 | 4.7812 |  | 15.1812 | 4 | 15.1812 | 69.8824 | 34.9412 | 15 | 35 | -0.058801 | -0.082215 | 1.1819e-05 | -1.2314e-05 | -1 | 0
851 | 14.1833 | 5 | 12 | 5 | 12 | 69.8842 | 40 | 7.6451e-06 | 3.534 | 1.9464e-05 | 0.00010636 | 4.7814 | 0 | 4.7815 |  | 15.1815 | 4 | 15.1815 | 69.8842 | 34.9421 | 15 | 35 | -0.057923 | -0.14014 | 7.6451e-06 | -1.2165e-05 | -1 | 0
852 | 14.2 | 5 | 12 | 5 | 12 | 69.8861 | 40 | 2.6846e-05 | 3.5341 | 1.92e-05 | 0.00037346 | 4.7814 | 0 | 4.7818 |  | 15.1818 | 4 | 15.1818 | 69.8861 | 34.943 | 15 | 35 | -0.056975 | -0.19711 | 2.6846e-05 | -1.2e-05 | -1 | 0
853 | 14.2167 | 5 | 12 | 5 | 12 | 69.8881 | 40 | 4.5759e-05 | 3.5341 | 1.8914e-05 | 0.00063658 | 4.7815 | 0 | 4.7821 |  | 15.1821 | 4 | 15.1821 | 69.8881 | 34.944 | 15 | 35 | -0.055959 | -0.25307 | 4.5759e-05 | -1.1821e-05 | -1 | 0
854 | 14.2333 | 5 | 11.9999 | 5 | 12 | 69.8902 | 40 | 6.4363e-05 | 3.5342 | 1.8604e-05 | 0.00089539 | 4.7815 | 0 | 4.7824 |  | 15.1824 | 4 | 15.1824 | 69.8902 | 34.9451 | 15 | 35 | -0.054878 | -0.30795 | 6.4363e-05 | -1.1627e-05 | -1 | 0
855 | 14.25 | 4.9999 | 11.9999 | 5 | 12 | 69.8925 | 40 | 8.2635e-05 | 3.5343 | 1.8272e-05 | 0.0011496 | 4.7817 | 0 | 4.7828 |  | 15.1828 | 4 | 15.1828 | 69.8925 | 34.9463 | 15 | 35 | -0.053734 | -0.36168 | 8.2635e-05 | -1.142e-05 | -1 | 0
856 | 14.2667 | 4.9999 | 11.9999 | 5 | 12 | 69.8949 | 40 | 0.00010055 | 3.5344 | 1.7919e-05 | 0.0013989 | 4.7818 | 0 | 4.7832 |  | 15.1832 | 4 | 15.1832 | 69.8949 | 34.9475 | 15 | 35 | -0.05253 | -0.41421 | 0.00010055 | -1.12e-05 | -1 | 0
857 | 14.2833 | 4.9999 | 11.9999 | 5 | 12 | 69.8975 | 40 | 0.0001181 | 3.5345 | 1.7546e-05 | 0.001643 | 4.782 | 0 | 4.7836 |  | 15.1836 | 4 | 15.1836 | 69.8975 | 34.9487 | 15 | 35 | -0.051268 | -0.46548 | 0.0001181 | -1.0966e-05 | -1 | 0
858 | 14.3 | 4.9999 | 11.9999 | 5 | 12 | 69.9001 | 40 | 0.00013525 | 3.5346 | 1.7153e-05 | 0.0018816 | 4.7821 | 0 | 4.784 |  | 15.184 | 4 | 15.184 | 69.9001 | 34.95 | 15 | 35 | -0.04995 | -0.51543 | 0.00013525 | -1.072e-05 | -1 | 0
859 | 14.3167 | 4.9999 | 11.9998 | 5 | 12 | 69.9028 | 40 | 0.00015199 | 3.5348 | 1.6741e-05 | 0.0021145 | 4.7823 | 0 | 4.7845 |  | 15.1845 | 4 | 15.1845 | 69.9028 | 34.9514 | 15 | 35 | -0.04858 | -0.56401 | 0.00015199 | -1.0463e-05 | -1 | 0
860 | 14.3333 | 4.9999 | 11.9998 | 5 | 12 | 69.9057 | 40 | 0.0001683 | 3.5349 | 1.631e-05 | 0.0023414 | 4.7826 | 0 | 4.7849 |  | 15.1849 | 4 | 15.1849 | 69.9057 | 34.9528 | 15 | 35 | -0.047159 | -0.61117 | 0.0001683 | -1.0194e-05 | -1 | 0
861 | 14.35 | 4.9999 | 11.9998 | 5 | 12 | 69.9086 | 40 | 0.00018417 | 3.5351 | 1.5863e-05 | 0.0025621 | 4.7828 | 0 | 4.7854 |  | 15.1854 | 4 | 15.1854 | 69.9086 | 34.9543 | 15 | 35 | -0.045691 | -0.65686 | 0.00018417 | -9.9143e-06 | -1 | 0
862 | 14.3667 | 4.9999 | 11.9998 | 5 | 12 | 69.9116 | 40 | 0.00019957 | 3.5353 | 1.5399e-05 | 0.0027763 | 4.7831 | 0 | 4.7859 |  | 15.1859 | 4 | 15.1859 | 69.9116 | 34.9558 | 15 | 35 | -0.044178 | -0.70104 | 0.00019957 | -9.6244e-06 | -1 | 0
863 | 14.3833 | 4.9999 | 11.9998 | 5 | 12 | 69.9148 | 40 | 0.00021449 | 3.5355 | 1.492e-05 | 0.0029838 | 4.7834 | 0 | 4.7864 |  | 15.1864 | 4 | 15.1864 | 69.9148 | 34.9574 | 15 | 35 | -0.042622 | -0.74366 | 0.00021449 | -9.3247e-06 | -1 | 0
864 | 14.4 | 4.9999 | 11.9998 | 5 | 12 | 69.9179 | 40 | 0.00022891 | 3.5358 | 1.4425e-05 | 0.0031845 | 4.7837 | 0 | 4.7869 |  | 15.1869 | 4 | 15.1869 | 69.9179 | 34.959 | 15 | 35 | -0.041028 | -0.78469 | 0.00022891 | -9.0159e-06 | -1 | 0
865 | 14.4167 | 4.9998 | 11.9998 | 5 | 12 | 69.9212 | 40 | 0.00024283 | 3.536 | 1.3918e-05 | 0.0033781 | 4.784 | 0 | 4.7874 |  | 15.1874 | 4 | 15.1874 | 69.9212 | 34.9606 | 15 | 35 | -0.039396 | -0.82409 | 0.00024283 | -8.6985e-06 | -1 | 0
866 | 14.4333 | 4.9998 | 11.9997 | 5 | 12 | 69.9245 | 40 | 0.00025623 | 3.5363 | 1.3397e-05 | 0.0035645 | 4.7844 | 0 | 4.7879 |  | 15.1879 | 4 | 15.1879 | 69.9245 | 34.9623 | 15 | 35 | -0.03773 | -0.86182 | 0.00025623 | -8.373e-06 | -1 | 0
867 | 14.45 | 4.9998 | 11.9997 | 5 | 12 | 69.9279 | 40 | 0.00026909 | 3.5365 | 1.2864e-05 | 0.0037435 | 4.7847 | 0 | 4.7885 |  | 15.1885 | 4 | 15.1885 | 69.9279 | 34.964 | 15 | 35 | -0.036033 | -0.89785 | 0.00026909 | -8.04e-06 | -1 | 0
868 | 14.4667 | 4.9998 | 11.9997 | 5 | 12 | 69.9314 | 40 | 0.00028141 | 3.5368 | 1.232e-05 | 0.0039148 | 4.7851 | 0 | 4.789 |  | 15.189 | 4 | 15.189 | 69.9314 | 34.9657 | 15 | 35 | -0.034308 | -0.93216 | 0.00028141 | -7.7e-06 | -1 | 0
869 | 14.4833 | 4.9998 | 11.9997 | 5 | 12 | 69.9349 | 40 | 0.00029318 | 3.5371 | 1.1766e-05 | 0.0040785 | 4.7855 | 0 | 4.7896 |  | 15.1896 | 4 | 15.1896 | 69.9349 | 34.9674 | 15 | 35 | -0.032557 | -0.96471 | 0.00029318 | -7.3537e-06 | -1 | 0
870 | 14.5 | 4.9998 | 11.9997 | 5 | 12 | 69.9384 | 40 | 0.00030438 | 3.5374 | 1.1203e-05 | 0.0042344 | 4.7859 | 0 | 4.7901 |  | 15.1901 | 4 | 15.1901 | 69.9384 | 34.9692 | 15 | 35 | -0.030783 | -0.9955 | 0.00030438 | -7.0016e-06 | -1 | 0
871 | 14.5167 | 4.9998 | 11.9997 | 5 | 12 | 69.942 | 40 | 0.00031501 | 3.5377 | 1.0631e-05 | 0.0043823 | 4.7863 | 0 | 4.7907 |  | 15.1907 | 4 | 15.1907 | 69.942 | 34.971 | 15 | 35 | -0.028989 | -1.0245 | 0.00031501 | -6.6442e-06 | -1 | 0
872 | 14.5333 | 4.9998 | 11.9997 | 5 | 12 | 69.9456 | 40 | 0.00032506 | 3.5381 | 1.0052e-05 | 0.0045221 | 4.7868 | 0 | 4.7913 |  | 15.1913 | 4 | 15.1913 | 69.9456 | 34.9728 | 15 | 35 | -0.027178 | -1.0517 | 0.00032506 | -6.2822e-06 | -1 | 0
873 | 14.55 | 4.9998 | 11.9997 | 5 | 12 | 69.9493 | 40 | 0.00033453 | 3.5384 | 9.4658e-06 | 0.0046538 | 4.7872 | 0 | 4.7919 |  | 15.1919 | 4 | 15.1919 | 69.9493 | 34.9746 | 15 | 35 | -0.025352 | -1.077 | 0.00033453 | -5.9161e-06 | -1 | 0
874 | 14.5667 | 4.9998 | 11.9997 | 5 | 12 | 69.953 | 40 | 0.0003434 | 3.5387 | 8.8743e-06 | 0.0047772 | 4.7877 | 0 | 4.7925 |  | 15.1925 | 4 | 15.1925 | 69.953 | 34.9765 | 15 | 35 | -0.023514 | -1.1005 | 0.0003434 | -5.5464e-06 | -1 | 0
875 | 14.5833 | 4.9998 | 11.9996 | 5 | 12 | 69.9567 | 40 | 0.00035168 | 3.5391 | 8.2781e-06 | 0.0048924 | 4.7882 | 0 | 4.7931 |  | 15.1931 | 4 | 15.1931 | 69.9567 | 34.9783 | 15 | 35 | -0.021667 | -1.1222 | 0.00035168 | -5.1738e-06 | -1 | 0
876 | 14.6 | 4.9998 | 11.9996 | 5 | 12 | 69.9604 | 40 | 0.00035936 | 3.5394 | 7.678e-06 | 0.0049992 | 4.7887 | 0 | 4.7937 |  | 15.1937 | 4 | 15.1937 | 69.9604 | 34.9802 | 15 | 35 | -0.019814 | -1.142 | 0.00035936 | -4.7988e-06 | -1 | 0
877 | 14.6167 | 4.9998 | 11.9996 | 5 | 12 | 69.9641 | 40 | 0.00036643 | 3.5398 | 7.075e-06 | 0.0050976 | 4.7892 | 0 | 4.7943 |  | 15.1943 | 4 | 15.1943 | 69.9641 | 34.982 | 15 | 35 | -0.017957 | -1.16 | 0.00036643 | -4.4219e-06 | -1 | 0
878 | 14.6333 | 4.9998 | 11.9996 | 5 | 12 | 69.9678 | 40 | 0.0003729 | 3.5402 | 6.4699e-06 | 0.0051876 | 4.7897 | 0 | 4.7948 |  | 15.1948 | 4 | 15.1948 | 69.9678 | 34.9839 | 15 | 35 | -0.016099 | -1.1761 | 0.0003729 | -4.0437e-06 | -1 | 0
879 | 14.65 | 4.9998 | 11.9996 | 5 | 12 | 69.9715 | 40 | 0.00037876 | 3.5406 | 5.8636e-06 | 0.0052692 | 4.7902 | 0 | 4.7954 |  | 15.1954 | 4 | 15.1954 | 69.9715 | 34.9858 | 15 | 35 | -0.014243 | -1.1903 | 0.00037876 | -3.6648e-06 | -1 | 0
880 | 14.6667 | 4.9998 | 11.9996 | 5 | 12 | 69.9752 | 40 | 0.00038402 | 3.5409 | 5.257e-06 | 0.0053423 | 4.7907 | 0 | 4.796 |  | 15.196 | 4 | 15.196 | 69.9752 | 34.9876 | 15 | 35 | -0.012391 | -1.2027 | 0.00038402 | -3.2856e-06 | -1 | 0
881 | 14.6833 | 4.9998 | 11.9996 | 5 | 12 | 69.9789 | 40 | 0.00038867 | 3.5413 | 4.6508e-06 | 0.005407 | 4.7912 | 0 | 4.7966 |  | 15.1966 | 4 | 15.1966 | 69.9789 | 34.9895 | 15 | 35 | -0.010545 | -1.2132 | 0.00038867 | -2.9068e-06 | -1 | 0
882 | 14.7 | 4.9998 | 11.9996 | 5 | 12 | 69.9826 | 40 | 0.00039272 | 3.5417 | 4.046e-06 | 0.0054633 | 4.7917 | 0 | 4.7972 |  | 15.1972 | 4 | 15.1972 | 69.9826 | 34.9913 | 15 | 35 | -0.0087092 | -1.222 | 0.00039272 | -2.5288e-06 | -1 | 0
883 | 14.7167 | 4.9998 | 11.9996 | 5 | 12 | 69.9862 | 40 | 0.00039616 | 3.5421 | 3.4434e-06 | 0.0055112 | 4.7923 | 0 | 4.7978 |  | 15.1978 | 4 | 15.1978 | 69.9862 | 34.9931 | 15 | 35 | -0.0068846 | -1.2288 | 0.00039616 | -2.1521e-06 | -1 | 0
884 | 14.7333 | 4.9998 | 11.9996 | 5 | 12 | 69.9899 | 40 | 0.00039901 | 3.5425 | 2.8438e-06 | 0.0055508 | 4.7928 | 0 | 4.7984 |  | 15.1984 | 4 | 15.1984 | 69.9899 | 34.9949 | 15 | 35 | -0.0050739 | -1.2339 | 0.00039901 | -1.7774e-06 | -1 | 0
885 | 14.75 | 4.9997 | 11.9996 | 5 | 12 | 69.9934 | 40 | 0.00040125 | 3.5429 | 2.248e-06 | 0.0055821 | 4.7934 | 0 | 4.799 |  | 15.199 | 4 | 15.199 | 69.9934 | 34.9967 | 15 | 35 | -0.0032797 | -1.2372 | 0.00040125 | -1.405e-06 | -1 | 0
886 | 14.7667 | 4.9997 | 11.9996 | 5 | 12 | 69.997 | 40 | 0.00040291 | 3.5433 | 1.6568e-06 | 0.0056051 | 4.7939 | 0 | 4.7995 |  | 15.1995 | 4 | 15.1995 | 69.997 | 34.9985 | 15 | 35 | -0.0015042 | -1.2387 | 0.00040291 | -1.0355e-06 | -1 | 0
887 | 14.7833 | 4.9997 | 11.9996 | 5 | 12 | 70.0005 | 40 | 0.00040398 | 3.5437 | 1.0709e-06 | 0.00562 | 4.7945 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0005 | 35.0003 | 15 | 35 | 0.00025034 | -1.2384 | 0.00040398 | -6.6934e-07 | -1 | 0
888 | 14.8 | 4.9997 | 11.9996 | 5 | 12 | 70.004 | 40 | 0.00040447 | 3.5441 | 4.9118e-07 | 0.0056268 | 4.795 | 0 | 4.8006 |  | 15.2006 | 4 | 15.2006 | 70.004 | 35.002 | 15 | 35 | 0.0019818 | -1.2365 | 0.00040447 | -3.0699e-07 | -1 | 0
889 | 14.8167 | 4.9997 | 11.9996 | 5 | 12 | 70.0074 | 40 | 0.00040439 | 3.5445 | -8.1743e-08 | 0.0056257 | 4.7956 | 0 | 4.8012 |  | 15.2012 | 4 | 15.2012 | 70.0074 | 35.0037 | 15 | 35 | 0.003688 | -1.2328 | 0.00040439 | 5.1089e-08 | 1 | 2
890 | 14.8333 | 4.9997 | 11.9996 | 5 | 12 | 70.0107 | 40 | 0.00040374 | 3.5449 | -6.4711e-07 | 0.0056167 | 4.7961 | 0 | 4.8017 |  | 15.2017 | 4 | 15.2017 | 70.0107 | 35.0054 | 15 | 35 | 0.0053668 | -1.2274 | 0.00040374 | 4.0444e-07 | 1 | 0
891 | 14.85 | 4.9997 | 11.9996 | 5 | 12 | 70.014 | 40 | 0.00040254 | 3.5453 | -1.2042e-06 | 0.0056 | 4.7966 | 0 | 4.8022 |  | 15.2022 | 4 | 15.2022 | 70.014 | 35.007 | 15 | 35 | 0.0070164 | -1.2204 | 0.00040254 | 7.5265e-07 | 1 | 0
892 | 14.8667 | 4.9997 | 11.9996 | 5 | 12 | 70.0173 | 40 | 0.00040079 | 3.5457 | -1.7524e-06 | 0.0055756 | 4.7972 | 0 | 4.8028 |  | 15.2028 | 4 | 15.2028 | 70.0173 | 35.0086 | 15 | 35 | 0.0086347 | -1.2118 | 0.00040079 | 1.0953e-06 | 1 | 0
893 | 14.8833 | 4.9998 | 11.9996 | 5 | 12 | 70.0204 | 40 | 0.0003985 | 3.5461 | -2.2911e-06 | 0.0055437 | 4.7977 | 0 | 4.8033 |  | 15.2033 | 4 | 15.2033 | 70.0204 | 35.0102 | 15 | 35 | 0.01022 | -1.2015 | 0.0003985 | 1.4319e-06 | 1 | 0
894 | 14.9 | 4.9998 | 11.9996 | 5 | 12 | 70.0235 | 40 | 0.00039568 | 3.5465 | -2.8195e-06 | 0.0055045 | 4.7983 | 0 | 4.8038 |  | 15.2038 | 4 | 15.2038 | 70.0235 | 35.0118 | 15 | 35 | 0.01177 | -1.1898 | 0.00039568 | 1.7622e-06 | 1 | 0
895 | 14.9167 | 4.9998 | 11.9996 | 5 | 12 | 70.0266 | 40 | 0.00039234 | 3.5469 | -3.3371e-06 | 0.0054581 | 4.7988 | 0 | 4.8043 |  | 15.2043 | 4 | 15.2043 | 70.0266 | 35.0133 | 15 | 35 | 0.013284 | -1.1765 | 0.00039234 | 2.0857e-06 | 1 | 0
896 | 14.9333 | 4.9998 | 11.9996 | 5 | 12 | 70.0295 | 40 | 0.0003885 | 3.5473 | -3.8434e-06 | 0.0054046 | 4.7993 | 0 | 4.8047 |  | 15.2047 | 4 | 15.2047 | 70.0295 | 35.0148 | 15 | 35 | 0.014759 | -1.1617 | 0.0003885 | 2.4021e-06 | 1 | 0
897 | 14.95 | 4.9998 | 11.9996 | 5 | 12 | 70.0324 | 40 | 0.00038416 | 3.5477 | -4.3376e-06 | 0.0053442 | 4.7998 | 0 | 4.8052 |  | 15.2052 | 4 | 15.2052 | 70.0324 | 35.0162 | 15 | 35 | 0.016195 | -1.1455 | 0.00038416 | 2.711e-06 | 1 | 0
898 | 14.9667 | 4.9998 | 11.9996 | 5 | 12 | 70.0352 | 40 | 0.00037934 | 3.5481 | -4.8194e-06 | 0.0052772 | 4.8004 | 0 | 4.8056 |  | 15.2056 | 4 | 15.2056 | 70.0352 | 35.0176 | 15 | 35 | 0.017589 | -1.1279 | 0.00037934 | 3.0121e-06 | 1 | 0
899 | 14.9833 | 4.9998 | 11.9996 | 5 | 12 | 70.0379 | 40 | 0.00037405 | 3.5485 | -5.2882e-06 | 0.0052036 | 4.8009 | 0 | 4.8061 |  | 15.2061 | 4 | 15.2061 | 70.0379 | 35.0189 | 15 | 35 | 0.018941 | -1.109 | 0.00037405 | 3.3051e-06 | 1 | 0
900 | 15 | 4.9998 | 11.9996 | 5 | 12 | 70.0405 | 40 | 0.00036831 | 3.5488 | -5.7435e-06 | 0.0051237 | 4.8014 | 0 | 4.8065 |  | 15.2065 | 4 | 15.2065 | 70.0405 | 35.0202 | 15 | 35 | 0.020248 | -1.0888 | 0.00036831 | 3.5897e-06 | 1 | 0
901 | 15.0167 | 4.9998 | 11.9996 | 5 | 12 | 70.043 | 40 | 0.00036212 | 3.5492 | -6.1848e-06 | 0.0050377 | 4.8018 | 0 | 4.8069 |  | 15.2069 | 4 | 15.2069 | 70.043 | 35.0215 | 15 | 35 | 0.021511 | -1.0672 | 0.00036212 | 3.8655e-06 | 1 | 0
902 | 15.0333 | 4.9998 | 11.9996 | 5 | 12 | 70.0455 | 40 | 0.00035551 | 3.5495 | -6.6117e-06 | 0.0049457 | 4.8023 | 0 | 4.8073 |  | 15.2073 | 4 | 15.2073 | 70.0455 | 35.0227 | 15 | 35 | 0.022726 | -1.0445 | 0.00035551 | 4.1323e-06 | 1 | 0
903 | 15.05 | 4.9998 | 11.9997 | 5 | 12 | 70.0478 | 40 | 0.00034849 | 3.5499 | -7.0239e-06 | 0.004848 | 4.8028 | 0 | 4.8076 |  | 15.2076 | 4 | 15.2076 | 70.0478 | 35.0239 | 15 | 35 | 0.023894 | -1.0206 | 0.00034849 | 4.3899e-06 | 1 | 0
904 | 15.0667 | 4.9998 | 11.9997 | 5 | 12 | 70.05 | 40 | 0.00034107 | 3.5502 | -7.4208e-06 | 0.0047448 | 4.8033 | 0 | 4.808 |  | 15.208 | 4 | 15.208 | 70.05 | 35.025 | 15 | 35 | 0.025014 | -0.99561 | 0.00034107 | 4.638e-06 | 1 | 0
905 | 15.0833 | 4.9998 | 11.9997 | 5 | 12 | 70.0522 | 40 | 0.00033326 | 3.5506 | -7.8022e-06 | 0.0046362 | 4.8037 | 0 | 4.8083 |  | 15.2083 | 4 | 15.2083 | 70.0522 | 35.0261 | 15 | 35 | 0.026083 | -0.96952 | 0.00033326 | 4.8764e-06 | 1 | 0
906 | 15.1 | 4.9998 | 11.9997 | 5 | 12 | 70.0542 | 40 | 0.0003251 | 3.5509 | -8.1677e-06 | 0.0045226 | 4.8042 | 0 | 4.8087 |  | 15.2087 | 4 | 15.2087 | 70.0542 | 35.0271 | 15 | 35 | 0.027103 | -0.94242 | 0.0003251 | 5.1048e-06 | 1 | 0
907 | 15.1167 | 4.9998 | 11.9997 | 5 | 12 | 70.0561 | 40 | 0.00031658 | 3.5512 | -8.5171e-06 | 0.0044041 | 4.8046 | 0 | 4.809 |  | 15.209 | 4 | 15.209 | 70.0561 | 35.0281 | 15 | 35 | 0.028071 | -0.91435 | 0.00031658 | 5.3232e-06 | 1 | 0
908 | 15.1333 | 4.9998 | 11.9997 | 5 | 12 | 70.058 | 40 | 0.00030773 | 3.5515 | -8.8499e-06 | 0.004281 | 4.805 | 0 | 4.8093 |  | 15.2093 | 4 | 15.2093 | 70.058 | 35.029 | 15 | 35 | 0.028987 | -0.88536 | 0.00030773 | 5.5312e-06 | 1 | 0
909 | 15.15 | 4.9998 | 11.9997 | 5 | 12 | 70.0597 | 40 | 0.00029856 | 3.5518 | -9.1661e-06 | 0.0041535 | 4.8054 | 0 | 4.8096 |  | 15.2096 | 4 | 15.2096 | 70.0597 | 35.0299 | 15 | 35 | 0.029851 | -0.85551 | 0.00029856 | 5.7288e-06 | 1 | 0
910 | 15.1667 | 4.9998 | 11.9997 | 5 | 12 | 70.0613 | 40 | 0.0002891 | 3.5521 | -9.4653e-06 | 0.0040218 | 4.8058 | 0 | 4.8098 |  | 15.2098 | 4 | 15.2098 | 70.0613 | 35.0307 | 15 | 35 | 0.030662 | -0.82485 | 0.0002891 | 5.9158e-06 | 1 | 0
911 | 15.1833 | 4.9998 | 11.9997 | 5 | 12 | 70.0628 | 40 | 0.00027935 | 3.5524 | -9.7474e-06 | 0.0038862 | 4.8062 | 0 | 4.8101 |  | 15.2101 | 4 | 15.2101 | 70.0628 | 35.0314 | 15 | 35 | 0.031419 | -0.79343 | 0.00027935 | 6.0921e-06 | 1 | 0
912 | 15.2 | 4.9998 | 11.9997 | 5 | 12 | 70.0642 | 40 | 0.00026934 | 3.5527 | -1.0012e-05 | 0.0037469 | 4.8065 | 0 | 4.8103 |  | 15.2103 | 4 | 15.2103 | 70.0642 | 35.0321 | 15 | 35 | 0.032123 | -0.76131 | 0.00026934 | 6.2576e-06 | 1 | 0
913 | 15.2167 | 4.9998 | 11.9997 | 5 | 12 | 70.0655 | 40 | 0.00025908 | 3.5529 | -1.0259e-05 | 0.0036042 | 4.8069 | 0 | 4.8105 |  | 15.2105 | 4 | 15.2105 | 70.0655 | 35.0328 | 15 | 35 | 0.032772 | -0.72854 | 0.00025908 | 6.4121e-06 | 1 | 0
914 | 15.2333 | 4.9998 | 11.9998 | 5 | 12 | 70.0667 | 40 | 0.00024859 | 3.5532 | -1.0489e-05 | 0.0034583 | 4.8072 | 0 | 4.8107 |  | 15.2107 | 4 | 15.2107 | 70.0667 | 35.0334 | 15 | 35 | 0.033367 | -0.69517 | 0.00024859 | 6.5557e-06 | 1 | 0
915 | 15.25 | 4.9999 | 11.9998 | 5 | 12 | 70.0678 | 40 | 0.00023789 | 3.5534 | -1.0701e-05 | 0.0033094 | 4.8075 | 0 | 4.8109 |  | 15.2109 | 4 | 15.2109 | 70.0678 | 35.0339 | 15 | 35 | 0.033908 | -0.66126 | 0.00023789 | 6.6882e-06 | 1 | 0
916 | 15.2667 | 4.9999 | 11.9998 | 5 | 12 | 70.0688 | 40 | 0.00022699 | 3.5536 | -1.0895e-05 | 0.0031578 | 4.8078 | 0 | 4.811 |  | 15.211 | 4 | 15.211 | 70.0688 | 35.0344 | 15 | 35 | 0.034394 | -0.62687 | 0.00022699 | 6.8096e-06 | 1 | 0
917 | 15.2833 | 4.9999 | 11.9998 | 5 | 12 | 70.0697 | 40 | 0.00021592 | 3.5538 | -1.1072e-05 | 0.0030038 | 4.8081 | 0 | 4.8111 |  | 15.2111 | 4 | 15.2111 | 70.0697 | 35.0348 | 15 | 35 | 0.034825 | -0.59204 | 0.00021592 | 6.92e-06 | 1 | 0
918 | 15.3 | 4.9999 | 11.9998 | 5 | 12 | 70.0704 | 40 | 0.00020469 | 3.554 | -1.1231e-05 | 0.0028476 | 4.8084 | 0 | 4.8113 |  | 15.2113 | 4 | 15.2113 | 70.0704 | 35.0352 | 15 | 35 | 0.035203 | -0.55684 | 0.00020469 | 7.0192e-06 | 1 | 0
919 | 15.3167 | 4.9999 | 11.9998 | 5 | 12 | 70.0711 | 40 | 0.00019332 | 3.5542 | -1.1372e-05 | 0.0026894 | 4.8087 | 0 | 4.8114 |  | 15.2114 | 4 | 15.2114 | 70.0711 | 35.0355 | 15 | 35 | 0.035526 | -0.52131 | 0.00019332 | 7.1072e-06 | 1 | 0
920 | 15.3333 | 4.9999 | 11.9998 | 5 | 12 | 70.0716 | 40 | 0.00018182 | 3.5544 | -1.1495e-05 | 0.0025295 | 4.8089 | 0 | 4.8115 |  | 15.2115 | 4 | 15.2115 | 70.0716 | 35.0358 | 15 | 35 | 0.035795 | -0.48552 | 0.00018182 | 7.1842e-06 | 1 | 0
921 | 15.35 | 4.9999 | 11.9998 | 5 | 12 | 70.072 | 40 | 0.00017022 | 3.5546 | -1.16e-05 | 0.0023681 | 4.8092 | 0 | 4.8115 |  | 15.2115 | 4 | 15.2115 | 70.072 | 35.036 | 15 | 35 | 0.03601 | -0.44951 | 0.00017022 | 7.2501e-06 | 1 | 0
922 | 15.3667 | 4.9999 | 11.9998 | 5 | 12 | 70.0723 | 40 | 0.00015854 | 3.5548 | -1.1688e-05 | 0.0022055 | 4.8094 | 0 | 4.8116 |  | 15.2116 | 4 | 15.2116 | 70.0723 | 35.0362 | 15 | 35 | 0.036172 | -0.41334 | 0.00015854 | 7.305e-06 | 1 | 0
923 | 15.3833 | 4.9999 | 11.9999 | 5 | 12 | 70.0726 | 40 | 0.00014678 | 3.5549 | -1.1758e-05 | 0.0020419 | 4.8096 | 0 | 4.8116 |  | 15.2116 | 4 | 15.2116 | 70.0726 | 35.0363 | 15 | 35 | 0.036282 | -0.37705 | 0.00014678 | 7.349e-06 | 1 | 0
924 | 15.4 | 4.9999 | 11.9999 | 5 | 12 | 70.0727 | 40 | 0.00013497 | 3.555 | -1.1811e-05 | 0.0018776 | 4.8098 | 0 | 4.8116 |  | 15.2116 | 4 | 15.2116 | 70.0727 | 35.0363 | 15 | 35 | 0.036339 | -0.34072 | 0.00013497 | 7.3821e-06 | 1 | 0
925 | 15.4167 | 4.9999 | 11.9999 | 5 | 12 | 70.0727 | 40 | 0.00012312 | 3.5552 | -1.1847e-05 | 0.0017128 | 4.8099 | 0 | 4.8116 |  | 15.2116 | 4 | 15.2116 | 70.0727 | 35.0363 | 15 | 35 | 0.036344 | -0.30437 | 0.00012312 | 7.4044e-06 | 1 | 0
926 | 15.4333 | 4.9999 | 11.9999 | 5 | 12 | 70.0726 | 40 | 0.00011125 | 3.5553 | -1.1866e-05 | 0.0015477 | 4.8101 | 0 | 4.8116 |  | 15.2116 | 4 | 15.2116 | 70.0726 | 35.0363 | 15 | 35 | 0.036299 | -0.26807 | 0.00011125 | 7.4161e-06 | 1 | 0
927 | 15.45 | 4.9999 | 11.9999 | 5 | 12 | 70.0724 | 40 | 9.9387e-05 | 3.5554 | -1.1868e-05 | 0.0013826 | 4.8102 | 0 | 4.8116 |  | 15.2116 | 4 | 15.2116 | 70.0724 | 35.0362 | 15 | 35 | 0.036203 | -0.23187 | 9.9387e-05 | 7.4172e-06 | 1 | 0
928 | 15.4667 | 4.9999 | 11.9999 | 5 | 12 | 70.0721 | 40 | 8.7534e-05 | 3.5555 | -1.1853e-05 | 0.0012177 | 4.8103 | 0 | 4.8115 |  | 15.2115 | 4 | 15.2115 | 70.0721 | 35.0361 | 15 | 35 | 0.036058 | -0.19581 | 8.7534e-05 | 7.4079e-06 | 1 | 0
929 | 15.4833 | 5 | 11.9999 | 5 | 12 | 70.0717 | 40 | 7.5712e-05 | 3.5555 | -1.1821e-05 | 0.0010533 | 4.8104 | 0 | 4.8115 |  | 15.2115 | 4 | 15.2115 | 70.0717 | 35.0359 | 15 | 35 | 0.035864 | -0.15995 | 7.5712e-05 | 7.3884e-06 | 1 | 0
930 | 15.5 | 5 | 11.9999 | 5 | 12 | 70.0712 | 40 | 6.3938e-05 | 3.5556 | -1.1774e-05 | 0.00088948 | 4.8105 | 0 | 4.8114 |  | 15.2114 | 4 | 15.2114 | 70.0712 | 35.0356 | 15 | 35 | 0.035623 | -0.12432 | 6.3938e-05 | 7.3587e-06 | 1 | 0
931 | 15.5167 | 5 | 11.9999 | 5 | 12 | 70.0707 | 40 | 5.2228e-05 | 3.5556 | -1.1711e-05 | 0.00072657 | 4.8106 | 0 | 4.8113 |  | 15.2113 | 4 | 15.2113 | 70.0707 | 35.0353 | 15 | 35 | 0.035334 | -0.088991 | 5.2228e-05 | 7.3192e-06 | 1 | 0
932 | 15.5333 | 5 | 12 | 5 | 12 | 70.07 | 40 | 4.0596e-05 | 3.5557 | -1.1632e-05 | 0.00056475 | 4.8106 | 0 | 4.8112 |  | 15.2112 | 4 | 15.2112 | 70.07 | 35.035 | 15 | 35 | 0.035 | -0.053991 | 4.0596e-05 | 7.2699e-06 | 1 | 0
933 | 15.55 | 5 | 12 | 5 | 12 | 70.0692 | 40 | 2.9058e-05 | 3.5557 | -1.1538e-05 | 0.00040424 | 4.8107 | 0 | 4.8111 |  | 15.2111 | 4 | 15.2111 | 70.0692 | 35.0346 | 15 | 35 | 0.034621 | -0.019369 | 2.9058e-05 | 7.2111e-06 | 1 | 0
934 | 15.5667 | 5 | 12 | 5 | 12 | 70.0684 | 40 | 1.763e-05 | 3.5557 | -1.1429e-05 | 0.00024525 | 4.8107 | 0 | 4.8109 |  | 15.2109 | 4 | 15.2109 | 70.0684 | 35.0342 | 15 | 35 | 0.034199 | 0.01483 | 1.763e-05 | 7.1429e-06 | 1 | 0
935 | 15.5833 | 5 | 12 | 5 | 12 | 70.0675 | 40 | 6.3246e-06 | 3.5557 | -1.1305e-05 | 8.7985e-05 | 4.8107 | 0 | 4.8108 |  | 15.2108 | 4 | 15.2108 | 70.0675 | 35.0337 | 15 | 35 | 0.033734 | 0.048565 | 6.3246e-06 | 7.0656e-06 | 1 | 0
936 | 15.6 | 5 | 12 | 5 | 12 | 70.0665 | 40 | -4.8425e-06 | 3.5557 | -1.1167e-05 | -6.7366e-05 | 4.8107 | 0 | 4.8106 |  | 15.2106 | 4 | 15.2106 | 70.0665 | 35.0332 | 15 | 35 | 0.033228 | 0.081793 | 4.8425e-06 | 6.9794e-06 | 1 | 0
937 | 15.6167 | 5 | 12 | 5 | 12 | 70.0654 | 40 | -1.5858e-05 | 3.5557 | -1.1015e-05 | -0.00022061 | 4.8107 | 0 | 4.8105 |  | 15.2105 | 4 | 15.2105 | 70.0654 | 35.0327 | 15 | 35 | 0.032683 | 0.11448 | 1.5858e-05 | 6.8846e-06 | 1 | 0
938 | 15.6333 | 5 | 12 | 5 | 12 | 70.0642 | 40 | -2.6708e-05 | 3.5557 | -1.085e-05 | -0.00037155 | 4.8106 | 0 | 4.8103 |  | 15.2103 | 4 | 15.2103 | 70.0642 | 35.0321 | 15 | 35 | 0.032098 | 0.14657 | 2.6708e-05 | 6.7813e-06 | 1 | 0
939 | 15.65 | 5 | 12 | 5 | 12 | 70.063 | 40 | -3.738e-05 | 3.5557 | -1.0672e-05 | -0.00052001 | 4.8106 | 0 | 4.8101 |  | 15.2101 | 4 | 15.2101 | 70.063 | 35.0315 | 15 | 35 | 0.031476 | 0.17805 | 3.738e-05 | 6.6699e-06 | 1 | 0
940 | 15.6667 | 5 | 12 | 5 | 12 | 70.0616 | 40 | -4.7861e-05 | 3.5556 | -1.0481e-05 | -0.00066582 | 4.8105 | 0 | 4.8099 |  | 15.2099 | 4 | 15.2099 | 70.0616 | 35.0308 | 15 | 35 | 0.030818 | 0.20887 | 4.7861e-05 | 6.5506e-06 | 1 | 0
941 | 15.6833 | 5 | 12.0001 | 5 | 12 | 70.0603 | 40 | -5.8139e-05 | 3.5555 | -1.0278e-05 | -0.0008088 | 4.8104 | 0 | 4.8096 |  | 15.2096 | 4 | 15.2096 | 70.0603 | 35.0301 | 15 | 35 | 0.030125 | 0.23899 | 5.8139e-05 | 6.4237e-06 | 1 | 0
942 | 15.7 | 5 | 12.0001 | 5 | 12 | 70.0588 | 40 | -6.8202e-05 | 3.5555 | -1.0063e-05 | -0.00094879 | 4.8104 | 0 | 4.8094 |  | 15.2094 | 4 | 15.2094 | 70.0588 | 35.0294 | 15 | 35 | 0.0294 | 0.26839 | 6.8202e-05 | 6.2894e-06 | 1 | 0
943 | 15.7167 | 5 | 12.0001 | 5 | 12 | 70.0573 | 40 | -7.8038e-05 | 3.5554 | -9.8368e-06 | -0.0010856 | 4.8103 | 0 | 4.8092 |  | 15.2092 | 4 | 15.2092 | 70.0573 | 35.0286 | 15 | 35 | 0.028642 | 0.29703 | 7.8038e-05 | 6.148e-06 | 1 | 0
944 | 15.7333 | 5.0001 | 12.0001 | 5 | 12 | 70.0557 | 40 | -8.7638e-05 | 3.5553 | -9.5998e-06 | -0.0012192 | 4.8101 | 0 | 4.8089 |  | 15.2089 | 4 | 15.2089 | 70.0557 | 35.0279 | 15 | 35 | 0.027854 | 0.32489 | 8.7638e-05 | 5.9999e-06 | 1 | 0
945 | 15.75 | 5.0001 | 12.0001 | 5 | 12 | 70.0541 | 40 | -9.6991e-05 | 3.5552 | -9.3525e-06 | -0.0013493 | 4.81 | 0 | 4.8087 |  | 15.2087 | 4 | 15.2087 | 70.0541 | 35.027 | 15 | 35 | 0.027037 | 0.35193 | 9.6991e-05 | 5.8453e-06 | 1 | 0
946 | 15.7667 | 5.0001 | 12.0001 | 5 | 12 | 70.0524 | 40 | -0.00010609 | 3.5551 | -9.0952e-06 | -0.0014758 | 4.8099 | 0 | 4.8084 |  | 15.2084 | 4 | 15.2084 | 70.0524 | 35.0262 | 15 | 35 | 0.026193 | 0.37812 | 0.00010609 | 5.6845e-06 | 1 | 0
947 | 15.7833 | 5.0001 | 12.0001 | 5 | 12 | 70.0506 | 40 | -0.00011491 | 3.555 | -8.8285e-06 | -0.0015986 | 4.8097 | 0 | 4.8081 |  | 15.2081 | 4 | 15.2081 | 70.0506 | 35.0253 | 15 | 35 | 0.025324 | 0.40344 | 0.00011491 | 5.5178e-06 | 1 | 0
948 | 15.8 | 5.0001 | 12.0001 | 5 | 12 | 70.0489 | 40 | -0.00012347 | 3.5549 | -8.553e-06 | -0.0017176 | 4.8095 | 0 | 4.8078 |  | 15.2078 | 4 | 15.2078 | 70.0489 | 35.0244 | 15 | 35 | 0.02443 | 0.42787 | 0.00012347 | 5.3456e-06 | 1 | 0
949 | 15.8167 | 5.0001 | 12.0001 | 5 | 12 | 70.047 | 40 | -0.00013174 | 3.5547 | -8.269e-06 | -0.0018327 | 4.8094 | 0 | 4.8075 |  | 15.2075 | 4 | 15.2075 | 70.047 | 35.0235 | 15 | 35 | 0.023514 | 0.45139 | 0.00013174 | 5.1681e-06 | 1 | 0
950 | 15.8333 | 5.0001 | 12.0001 | 5 | 12 | 70.0452 | 40 | -0.00013971 | 3.5546 | -7.9771e-06 | -0.0019436 | 4.8092 | 0 | 4.8072 |  | 15.2072 | 4 | 15.2072 | 70.0452 | 35.0226 | 15 | 35 | 0.022576 | 0.47396 | 0.00013971 | 4.9857e-06 | 1 | 0
951 | 15.85 | 5.0001 | 12.0001 | 5 | 12 | 70.0432 | 40 | -0.00014739 | 3.5545 | -7.6779e-06 | -0.0020504 | 4.809 | 0 | 4.8069 |  | 15.2069 | 4 | 15.2069 | 70.0432 | 35.0216 | 15 | 35 | 0.021619 | 0.49558 | 0.00014739 | 4.7987e-06 | 1 | 0
952 | 15.8667 | 5.0001 | 12.0002 | 5 | 12 | 70.0413 | 40 | -0.00015476 | 3.5543 | -7.3718e-06 | -0.002153 | 4.8088 | 0 | 4.8066 |  | 15.2066 | 4 | 15.2066 | 70.0413 | 35.0206 | 15 | 35 | 0.020644 | 0.51623 | 0.00015476 | 4.6074e-06 | 1 | 0
953 | 15.8833 | 5.0001 | 12.0002 | 5 | 12 | 70.0393 | 40 | -0.00016182 | 3.5541 | -7.0593e-06 | -0.0022512 | 4.8085 | 0 | 4.8063 |  | 15.2063 | 4 | 15.2063 | 70.0393 | 35.0197 | 15 | 35 | 0.019653 | 0.53588 | 0.00016182 | 4.4121e-06 | 1 | 0
954 | 15.9 | 5.0001 | 12.0002 | 5 | 12 | 70.0373 | 40 | -0.00016856 | 3.554 | -6.741e-06 | -0.002345 | 4.8083 | 0 | 4.806 |  | 15.206 | 4 | 15.206 | 70.0373 | 35.0186 | 15 | 35 | 0.018647 | 0.55453 | 0.00016856 | 4.2131e-06 | 1 | 0
955 | 15.9167 | 5.0001 | 12.0002 | 5 | 12 | 70.0353 | 40 | -0.00017498 | 3.5538 | -6.4174e-06 | -0.0024343 | 4.8081 | 0 | 4.8056 |  | 15.2056 | 4 | 15.2056 | 70.0353 | 35.0176 | 15 | 35 | 0.017629 | 0.57216 | 0.00017498 | 4.0109e-06 | 1 | 0
956 | 15.9333 | 5.0001 | 12.0002 | 5 | 12 | 70.0332 | 40 | -0.00018107 | 3.5536 | -6.089e-06 | -0.002519 | 4.8078 | 0 | 4.8053 |  | 15.2053 | 4 | 15.2053 | 70.0332 | 35.0166 | 15 | 35 | 0.016598 | 0.58875 | 0.00018107 | 3.8056e-06 | 1 | 0
957 | 15.95 | 5.0001 | 12.0002 | 5 | 12 | 70.0311 | 40 | -0.00018683 | 3.5534 | -5.7563e-06 | -0.002599 | 4.8076 | 0 | 4.805 |  | 15.205 | 4 | 15.205 | 70.0311 | 35.0156 | 15 | 35 | 0.015558 | 0.60431 | 0.00018683 | 3.5977e-06 | 1 | 0
958 | 15.9667 | 5.0001 | 12.0002 | 5 | 12 | 70.029 | 40 | -0.00019225 | 3.5532 | -5.4199e-06 | -0.0026744 | 4.8073 | 0 | 4.8046 |  | 15.2046 | 4 | 15.2046 | 70.029 | 35.0145 | 15 | 35 | 0.01451 | 0.61882 | 0.00019225 | 3.3874e-06 | 1 | 0
959 | 15.9833 | 5.0001 | 12.0002 | 5 | 12 | 70.0269 | 40 | -0.00019733 | 3.553 | -5.0803e-06 | -0.0027451 | 4.8071 | 0 | 4.8043 |  | 15.2043 | 4 | 15.2043 | 70.0269 | 35.0135 | 15 | 35 | 0.013455 | 0.63228 | 0.00019733 | 3.1752e-06 | 1 | 0
960 | 16 | 5.0001 | 12.0002 | 5 | 12 | 70.0248 | 40 | -0.00020206 | 3.5528 | -4.7379e-06 | -0.002811 | 4.8068 | 0 | 4.804 |  | 15.204 | 4 | 15.204 | 70.0248 | 35.0124 | 15 | 35 | 0.012394 | 0.64467 | 0.00020206 | 2.9612e-06 | 1 | 0
961 | 16.0167 | 5.0001 | 12.0002 | 5 | 12 | 70.0227 | 40 | -0.00020646 | 3.5526 | -4.3934e-06 | -0.0028721 | 4.8065 | 0 | 4.8036 |  | 15.2036 | 4 | 15.2036 | 70.0227 | 35.0113 | 15 | 35 | 0.011331 | 0.656 | 0.00020646 | 2.7459e-06 | 1 | 0
962 | 16.0333 | 5.0001 | 12.0002 | 5 | 12 | 70.0205 | 40 | -0.0002105 | 3.5524 | -4.0472e-06 | -0.0029284 | 4.8062 | 0 | 4.8033 |  | 15.2033 | 4 | 15.2033 | 70.0205 | 35.0103 | 15 | 35 | 0.010265 | 0.66627 | 0.0002105 | 2.5295e-06 | 1 | 0
963 | 16.05 | 5.0001 | 12.0002 | 5 | 12 | 70.0184 | 40 | -0.0002142 | 3.5522 | -3.6998e-06 | -0.0029799 | 4.8059 | 0 | 4.8029 |  | 15.2029 | 4 | 15.2029 | 70.0184 | 35.0092 | 15 | 35 | 0.0091981 | 0.67546 | 0.0002142 | 2.3124e-06 | 1 | 0
964 | 16.0667 | 5.0001 | 12.0002 | 5 | 12 | 70.0163 | 40 | -0.00021756 | 3.552 | -3.3517e-06 | -0.0030265 | 4.8056 | 0 | 4.8026 |  | 15.2026 | 4 | 15.2026 | 70.0163 | 35.0081 | 15 | 35 | 0.0081326 | 0.6836 | 0.00021756 | 2.0948e-06 | 1 | 0
965 | 16.0833 | 5.0001 | 12.0002 | 5 | 12 | 70.0141 | 40 | -0.00022056 | 3.5518 | -3.0035e-06 | -0.0030683 | 4.8053 | 0 | 4.8023 |  | 15.2023 | 4 | 15.2023 | 70.0141 | 35.0071 | 15 | 35 | 0.0070695 | 0.69067 | 0.00022056 | 1.8772e-06 | 1 | 0
966 | 16.1 | 5.0001 | 12.0002 | 5 | 12 | 70.012 | 40 | -0.00022322 | 3.5515 | -2.6555e-06 | -0.0031053 | 4.805 | 0 | 4.8019 |  | 15.2019 | 4 | 15.2019 | 70.012 | 35.006 | 15 | 35 | 0.0060103 | 0.69668 | 0.00022322 | 1.6597e-06 | 1 | 0
967 | 16.1167 | 5.0001 | 12.0002 | 5 | 12 | 70.0099 | 40 | -0.00022552 | 3.5513 | -2.3084e-06 | -0.0031374 | 4.8047 | 0 | 4.8016 |  | 15.2016 | 4 | 15.2016 | 70.0099 | 35.005 | 15 | 35 | 0.0049564 | 0.70163 | 0.00022552 | 1.4428e-06 | 1 | 0
968 | 16.1333 | 5.0001 | 12.0002 | 5 | 12 | 70.0078 | 40 | -0.00022749 | 3.5511 | -1.9625e-06 | -0.0031647 | 4.8044 | 0 | 4.8013 |  | 15.2013 | 4 | 15.2013 | 70.0078 | 35.0039 | 15 | 35 | 0.0039093 | 0.70554 | 0.00022749 | 1.2266e-06 | 1 | 0
969 | 16.15 | 5.0001 | 12.0002 | 5 | 12 | 70.0057 | 40 | -0.0002291 | 3.5509 | -1.6184e-06 | -0.0031872 | 4.8041 | 0 | 4.8009 |  | 15.2009 | 4 | 15.2009 | 70.0057 | 35.0029 | 15 | 35 | 0.0028703 | 0.70841 | 0.0002291 | 1.0115e-06 | 1 | 0
970 | 16.1667 | 5.0001 | 12.0002 | 5 | 12 | 70.0037 | 40 | -0.00023038 | 3.5506 | -1.2765e-06 | -0.003205 | 4.8038 | 0 | 4.8006 |  | 15.2006 | 4 | 15.2006 | 70.0037 | 35.0018 | 15 | 35 | 0.0018408 | 0.71025 | 0.00023038 | 7.9782e-07 | 1 | 0
971 | 16.1833 | 5.0001 | 12.0002 | 5 | 12 | 70.0016 | 40 | -0.00023132 | 3.5504 | -9.3725e-07 | -0.003218 | 4.8035 | 0 | 4.8003 |  | 15.2003 | 4 | 15.2003 | 70.0016 | 35.0008 | 15 | 35 | 0.00082205 | 0.71108 | 0.00023132 | 5.8578e-07 | 1 | 0
972 | 16.2 | 5.0001 | 12.0002 | 5 | 12 | 69.9996 | 40 | -0.00023192 | 3.5502 | -6.0108e-07 | -0.0032264 | 4.8032 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9996 | 34.9998 | 15 | 35 | -0.00018463 | 0.71089 | 0.00023192 | 3.7567e-07 | 1 | 0
973 | 16.2167 | 5.0001 | 12.0002 | 5 | 12 | 69.9976 | 40 | -0.00023219 | 3.5499 | -2.6842e-07 | -0.0032301 | 4.8029 | 0 | 4.7996 |  | 15.1996 | 4 | 15.1996 | 69.9976 | 34.9988 | 15 | 35 | -0.001178 | 0.70971 | 0.00023219 | 1.6776e-07 | 1 | 0
974 | 16.2333 | 5.0001 | 12.0002 | 5 | 12 | 69.9957 | 40 | -0.00023213 | 3.5497 | 6.0286e-08 | -0.0032293 | 4.8025 | 0 | 4.7993 |  | 15.1993 | 4 | 15.1993 | 69.9957 | 34.9978 | 15 | 35 | -0.0021568 | 0.70756 | 0.00023213 | -3.7679e-08 | -1 | -2
975 | 16.25 | 5.0001 | 12.0002 | 5 | 12 | 69.9938 | 40 | -0.00023174 | 3.5495 | 3.8464e-07 | -0.0032239 | 4.8022 | 0 | 4.799 |  | 15.199 | 4 | 15.199 | 69.9938 | 34.9969 | 15 | 35 | -0.0031198 | 0.70444 | 0.00023174 | -2.404e-07 | -1 | 0
976 | 16.2667 | 5.0001 | 12.0002 | 5 | 12 | 69.9919 | 40 | -0.00023104 | 3.5492 | 7.0425e-07 | -0.0032141 | 4.8019 | 0 | 4.7987 |  | 15.1987 | 4 | 15.1987 | 69.9919 | 34.9959 | 15 | 35 | -0.004066 | 0.70037 | 0.00023104 | -4.4016e-07 | -1 | 0
977 | 16.2833 | 5.0001 | 12.0002 | 5 | 12 | 69.99 | 40 | -0.00023002 | 3.549 | 1.0187e-06 | -0.0031999 | 4.8016 | 0 | 4.7984 |  | 15.1984 | 4 | 15.1984 | 69.99 | 34.995 | 15 | 35 | -0.0049943 | 0.69538 | 0.00023002 | -6.367e-07 | -1 | 0
978 | 16.3 | 5.0001 | 12.0002 | 5 | 12 | 69.9882 | 40 | -0.00022869 | 3.5488 | 1.3277e-06 | -0.0031815 | 4.8013 | 0 | 4.7981 |  | 15.1981 | 4 | 15.1981 | 69.9882 | 34.9941 | 15 | 35 | -0.0059034 | 0.68947 | 0.00022869 | -8.2981e-07 | -1 | 0
979 | 16.3167 | 5.0001 | 12.0002 | 5 | 12 | 69.9864 | 40 | -0.00022706 | 3.5486 | 1.6308e-06 | -0.0031588 | 4.801 | 0 | 4.7978 |  | 15.1978 | 4 | 15.1978 | 69.9864 | 34.9932 | 15 | 35 | -0.0067926 | 0.68268 | 0.00022706 | -1.0192e-06 | -1 | 0
980 | 16.3333 | 5.0001 | 12.0002 | 5 | 12 | 69.9847 | 40 | -0.00022513 | 3.5483 | 1.9277e-06 | -0.003132 | 4.8007 | 0 | 4.7975 |  | 15.1975 | 4 | 15.1975 | 69.9847 | 34.9923 | 15 | 35 | -0.0076606 | 0.67502 | 0.00022513 | -1.2048e-06 | -1 | 0
981 | 16.35 | 5.0001 | 12.0002 | 5 | 12 | 69.983 | 40 | -0.00022292 | 3.5481 | 2.218e-06 | -0.0031011 | 4.8004 | 0 | 4.7973 |  | 15.1973 | 4 | 15.1973 | 69.983 | 34.9915 | 15 | 35 | -0.0085067 | 0.66651 | 0.00022292 | -1.3862e-06 | -1 | 0
982 | 16.3667 | 5.0001 | 12.0002 | 5 | 12 | 69.9813 | 40 | -0.00022041 | 3.5479 | 2.5014e-06 | -0.0030663 | 4.8001 | 0 | 4.797 |  | 15.197 | 4 | 15.197 | 69.9813 | 34.9907 | 15 | 35 | -0.0093298 | 0.65718 | 0.00022041 | -1.5634e-06 | -1 | 0
983 | 16.3833 | 5.0001 | 12.0002 | 5 | 12 | 69.9797 | 40 | -0.00021764 | 3.5477 | 2.7777e-06 | -0.0030277 | 4.7998 | 0 | 4.7968 |  | 15.1968 | 4 | 15.1968 | 69.9797 | 34.9899 | 15 | 35 | -0.010129 | 0.64705 | 0.00021764 | -1.7361e-06 | -1 | 0
984 | 16.4 | 5.0001 | 12.0002 | 5 | 12 | 69.9782 | 40 | -0.00021459 | 3.5475 | 3.0465e-06 | -0.0029853 | 4.7995 | 0 | 4.7965 |  | 15.1965 | 4 | 15.1965 | 69.9782 | 34.9891 | 15 | 35 | -0.010904 | 0.63615 | 0.00021459 | -1.904e-06 | -1 | 0
985 | 16.4167 | 5.0001 | 12.0002 | 5 | 12 | 69.9767 | 40 | -0.00021128 | 3.5472 | 3.3075e-06 | -0.0029393 | 4.7992 | 0 | 4.7963 |  | 15.1963 | 4 | 15.1963 | 69.9767 | 34.9883 | 15 | 35 | -0.011654 | 0.6245 | 0.00021128 | -2.0672e-06 | -1 | 0
986 | 16.4333 | 5.0001 | 12.0002 | 5 | 12 | 69.9752 | 40 | -0.00020772 | 3.547 | 3.5605e-06 | -0.0028897 | 4.7989 | 0 | 4.796 |  | 15.196 | 4 | 15.196 | 69.9752 | 34.9876 | 15 | 35 | -0.012377 | 0.61212 | 0.00020772 | -2.2253e-06 | -1 | 0
987 | 16.45 | 5.0001 | 12.0002 | 5 | 12 | 69.9739 | 40 | -0.00020392 | 3.5468 | 3.8052e-06 | -0.0028368 | 4.7987 | 0 | 4.7958 |  | 15.1958 | 4 | 15.1958 | 69.9739 | 34.9869 | 15 | 35 | -0.013074 | 0.59905 | 0.00020392 | -2.3783e-06 | -1 | 0
988 | 16.4667 | 5.0001 | 12.0002 | 5 | 12 | 69.9725 | 40 | -0.00019988 | 3.5466 | 4.0415e-06 | -0.0027806 | 4.7984 | 0 | 4.7956 |  | 15.1956 | 4 | 15.1956 | 69.9725 | 34.9863 | 15 | 35 | -0.013743 | 0.5853 | 0.00019988 | -2.5259e-06 | -1 | 0
989 | 16.4833 | 5.0001 | 12.0002 | 5 | 12 | 69.9712 | 40 | -0.00019561 | 3.5464 | 4.269e-06 | -0.0027212 | 4.7981 | 0 | 4.7954 |  | 15.1954 | 4 | 15.1954 | 69.9712 | 34.9856 | 15 | 35 | -0.014385 | 0.57092 | 0.00019561 | -2.6681e-06 | -1 | 0
990 | 16.5 | 5.0001 | 12.0002 | 5 | 12 | 69.97 | 40 | -0.00019112 | 3.5462 | 4.4875e-06 | -0.0026588 | 4.7979 | 0 | 4.7952 |  | 15.1952 | 4 | 15.1952 | 69.97 | 34.985 | 15 | 35 | -0.014997 | 0.55592 | 0.00019112 | -2.8047e-06 | -1 | 0
991 | 16.5167 | 5.0001 | 12.0002 | 5 | 12 | 69.9688 | 40 | -0.00018642 | 3.5461 | 4.697e-06 | -0.0025934 | 4.7976 | 0 | 4.795 |  | 15.195 | 4 | 15.195 | 69.9688 | 34.9844 | 15 | 35 | -0.015581 | 0.54034 | 0.00018642 | -2.9356e-06 | -1 | 0
992 | 16.5333 | 5.0001 | 12.0002 | 5 | 12 | 69.9677 | 40 | -0.00018152 | 3.5459 | 4.8971e-06 | -0.0025253 | 4.7974 | 0 | 4.7948 |  | 15.1948 | 4 | 15.1948 | 69.9677 | 34.9839 | 15 | 35 | -0.016136 | 0.5242 | 0.00018152 | -3.0607e-06 | -1 | 0
993 | 16.55 | 5.0001 | 12.0002 | 5 | 12 | 69.9667 | 40 | -0.00017644 | 3.5457 | 5.0878e-06 | -0.0024545 | 4.7971 | 0 | 4.7947 |  | 15.1947 | 4 | 15.1947 | 69.9667 | 34.9833 | 15 | 35 | -0.016661 | 0.50754 | 0.00017644 | -3.1799e-06 | -1 | 0
994 | 16.5667 | 5.0001 | 12.0002 | 5 | 12 | 69.9657 | 40 | -0.00017117 | 3.5455 | 5.2689e-06 | -0.0023812 | 4.7969 | 0 | 4.7945 |  | 15.1945 | 4 | 15.1945 | 69.9657 | 34.9828 | 15 | 35 | -0.017155 | 0.49039 | 0.00017117 | -3.2931e-06 | -1 | 0
995 | 16.5833 | 5.0001 | 12.0002 | 5 | 12 | 69.9648 | 40 | -0.00016573 | 3.5454 | 5.4403e-06 | -0.0023055 | 4.7967 | 0 | 4.7944 |  | 15.1944 | 4 | 15.1944 | 69.9648 | 34.9824 | 15 | 35 | -0.01762 | 0.47277 | 0.00016573 | -3.4002e-06 | -1 | 0
996 | 16.6 | 5.0001 | 12.0002 | 5 | 12 | 69.9639 | 40 | -0.00016013 | 3.5452 | 5.6018e-06 | -0.0022276 | 4.7965 | 0 | 4.7942 |  | 15.1942 | 4 | 15.1942 | 69.9639 | 34.9819 | 15 | 35 | -0.018053 | 0.45471 | 0.00016013 | -3.5011e-06 | -1 | 0
997 | 16.6167 | 5.0001 | 12.0002 | 5 | 12 | 69.9631 | 40 | -0.00015437 | 3.545 | 5.7533e-06 | -0.0021476 | 4.7962 | 0 | 4.7941 |  | 15.1941 | 4 | 15.1941 | 69.9631 | 34.9815 | 15 | 35 | -0.018456 | 0.43626 | 0.00015437 | -3.5958e-06 | -1 | 0
998 | 16.6333 | 5.0001 | 12.0001 | 5 | 12 | 69.9623 | 40 | -0.00014848 | 3.5449 | 5.8949e-06 | -0.0020656 | 4.796 | 0 | 4.794 |  | 15.194 | 4 | 15.194 | 69.9623 | 34.9812 | 15 | 35 | -0.018827 | 0.41743 | 0.00014848 | -3.6843e-06 | -1 | 0
999 | 16.65 | 5.0001 | 12.0001 | 5 | 12 | 69.9617 | 40 | -0.00014245 | 3.5448 | 6.0263e-06 | -0.0019817 | 4.7958 | 0 | 4.7939 |  | 15.1939 | 4 | 15.1939 | 69.9617 | 34.9808 | 15 | 35 | -0.019167 | 0.39826 | 0.00014245 | -3.7665e-06 | -1 | 0
1000 | 16.6667 | 5.0001 | 12.0001 | 5 | 12 | 69.961 | 40 | -0.0001363 | 3.5446 | 6.1476e-06 | -0.0018962 | 4.7957 | 0 | 4.7938 |  | 15.1938 | 4 | 15.1938 | 69.961 | 34.9805 | 15 | 35 | -0.019476 | 0.37879 | 0.0001363 | -3.8423e-06 | -1 | 0
1001 | 16.6833 | 5.0001 | 12.0001 | 5 | 12 | 69.9605 | 40 | -0.00013005 | 3.5445 | 6.2588e-06 | -0.0018091 | 4.7955 | 0 | 4.7937 |  | 15.1937 | 4 | 15.1937 | 69.9605 | 34.9802 | 15 | 35 | -0.019754 | 0.35903 | 0.00013005 | -3.9117e-06 | -1 | 0
1002 | 16.7 | 5.0001 | 12.0001 | 5 | 12 | 69.96 | 40 | -0.00012369 | 3.5444 | 6.3597e-06 | -0.0017207 | 4.7953 | 0 | 4.7936 |  | 15.1936 | 4 | 15.1936 | 69.96 | 34.98 | 15 | 35 | -0.020001 | 0.33903 | 0.00012369 | -3.9748e-06 | -1 | 0
1003 | 16.7167 | 5.0001 | 12.0001 | 5 | 12 | 69.9596 | 40 | -0.00011724 | 3.5443 | 6.4503e-06 | -0.0016309 | 4.7952 | 0 | 4.7935 |  | 15.1935 | 4 | 15.1935 | 69.9596 | 34.9798 | 15 | 35 | -0.020216 | 0.31882 | 0.00011724 | -4.0315e-06 | -1 | 0
1004 | 16.7333 | 5.0001 | 12.0001 | 5 | 12 | 69.9592 | 40 | -0.0001107 | 3.5441 | 6.5308e-06 | -0.0015401 | 4.795 | 0 | 4.7935 |  | 15.1935 | 4 | 15.1935 | 69.9592 | 34.9796 | 15 | 35 | -0.0204 | 0.29842 | 0.0001107 | -4.0818e-06 | -1 | 0
1005 | 16.75 | 5.0001 | 12.0001 | 5 | 12 | 69.9589 | 40 | -0.0001041 | 3.544 | 6.6011e-06 | -0.0014482 | 4.7949 | 0 | 4.7934 |  | 15.1934 | 4 | 15.1934 | 69.9589 | 34.9794 | 15 | 35 | -0.020553 | 0.27786 | 0.0001041 | -4.1257e-06 | -1 | 0
1006 | 16.7667 | 5.0001 | 12.0001 | 5 | 12 | 69.9586 | 40 | -9.7442e-05 | 3.5439 | 6.6612e-06 | -0.0013556 | 4.7947 | 0 | 4.7934 |  | 15.1934 | 4 | 15.1934 | 69.9586 | 34.9793 | 15 | 35 | -0.020676 | 0.25719 | 9.7442e-05 | -4.1633e-06 | -1 | 0
1007 | 16.7833 | 5.0001 | 12.0001 | 5 | 12 | 69.9585 | 40 | -9.0731e-05 | 3.5438 | 6.7112e-06 | -0.0012622 | 4.7946 | 0 | 4.7934 |  | 15.1934 | 4 | 15.1934 | 69.9585 | 34.9792 | 15 | 35 | -0.020767 | 0.23642 | 9.0731e-05 | -4.1945e-06 | -1 | 0
1008 | 16.8 | 5.0001 | 12.0001 | 5 | 12 | 69.9583 | 40 | -8.398e-05 | 3.5438 | 6.7512e-06 | -0.0011683 | 4.7945 | 0 | 4.7933 |  | 15.1933 | 4 | 15.1933 | 69.9583 | 34.9792 | 15 | 35 | -0.020829 | 0.21559 | 8.398e-05 | -4.2195e-06 | -1 | 0
1009 | 16.8167 | 5 | 12.0001 | 5 | 12 | 69.9583 | 40 | -7.7198e-05 | 3.5437 | 6.7812e-06 | -0.0010739 | 4.7944 | 0 | 4.7933 |  | 15.1933 | 4 | 15.1933 | 69.9583 | 34.9791 | 15 | 35 | -0.020861 | 0.19473 | 7.7198e-05 | -4.2382e-06 | -1 | 0
1010 | 16.8333 | 5 | 12.0001 | 5 | 12 | 69.9583 | 40 | -7.0397e-05 | 3.5436 | 6.8013e-06 | -0.00097933 | 4.7943 | 0 | 4.7933 |  | 15.1933 | 4 | 15.1933 | 69.9583 | 34.9791 | 15 | 35 | -0.020863 | 0.17387 | 7.0397e-05 | -4.2508e-06 | -1 | 0
1011 | 16.85 | 5 | 12.0001 | 5 | 12 | 69.9583 | 40 | -6.3585e-05 | 3.5436 | 6.8116e-06 | -0.00088457 | 4.7942 | 0 | 4.7933 |  | 15.1933 | 4 | 15.1933 | 69.9583 | 34.9792 | 15 | 35 | -0.020835 | 0.15303 | 6.3585e-05 | -4.2573e-06 | -1 | 0
1012 | 16.8667 | 5 | 12.0001 | 5 | 12 | 69.9584 | 40 | -5.6773e-05 | 3.5435 | 6.8123e-06 | -0.0007898 | 4.7941 | 0 | 4.7934 |  | 15.1934 | 4 | 15.1934 | 69.9584 | 34.9792 | 15 | 35 | -0.020779 | 0.13225 | 5.6773e-05 | -4.2577e-06 | -1 | 0
1013 | 16.8833 | 5 | 12 | 5 | 12 | 69.9586 | 40 | -4.997e-05 | 3.5434 | 6.8033e-06 | -0.00069516 | 4.7941 | 0 | 4.7934 |  | 15.1934 | 4 | 15.1934 | 69.9586 | 34.9793 | 15 | 35 | -0.020695 | 0.11156 | 4.997e-05 | -4.2521e-06 | -1 | 0
1014 | 16.9 | 5 | 12 | 5 | 12 | 69.9588 | 40 | -4.3185e-05 | 3.5434 | 6.785e-06 | -0.00060077 | 4.794 | 0 | 4.7934 |  | 15.1934 | 4 | 15.1934 | 69.9588 | 34.9794 | 15 | 35 | -0.020582 | 0.090977 | 4.3185e-05 | -4.2406e-06 | -1 | 0
1015 | 16.9167 | 5 | 12 | 5 | 12 | 69.9591 | 40 | -3.6427e-05 | 3.5434 | 6.7574e-06 | -0.00050676 | 4.794 | 0 | 4.7935 |  | 15.1935 | 4 | 15.1935 | 69.9591 | 34.9796 | 15 | 35 | -0.020442 | 0.070534 | 3.6427e-05 | -4.2234e-06 | -1 | 0
1016 | 16.9333 | 5 | 12 | 5 | 12 | 69.9594 | 40 | -2.9707e-05 | 3.5433 | 6.7207e-06 | -0.00041327 | 4.7939 | 0 | 4.7935 |  | 15.1935 | 4 | 15.1935 | 69.9594 | 34.9797 | 15 | 35 | -0.020276 | 0.050258 | 2.9707e-05 | -4.2005e-06 | -1 | 0
1017 | 16.95 | 5 | 12 | 5 | 12 | 69.9598 | 40 | -2.3032e-05 | 3.5433 | 6.6751e-06 | -0.00032041 | 4.7939 | 0 | 4.7936 |  | 15.1936 | 4 | 15.1936 | 69.9598 | 34.9799 | 15 | 35 | -0.020083 | 0.030175 | 2.3032e-05 | -4.1719e-06 | -1 | 0
1018 | 16.9667 | 5 | 12 | 5 | 12 | 69.9603 | 40 | -1.6411e-05 | 3.5433 | 6.6207e-06 | -0.0002283 | 4.7939 | 0 | 4.7936 |  | 15.1936 | 4 | 15.1936 | 69.9603 | 34.9801 | 15 | 35 | -0.019865 | 0.010311 | 1.6411e-05 | -4.1379e-06 | -1 | 0
1019 | 16.9833 | 5 | 12 | 5 | 12 | 69.9608 | 40 | -9.8532e-06 | 3.5433 | 6.5577e-06 | -0.00013707 | 4.7939 | 0 | 4.7937 |  | 15.1937 | 4 | 15.1937 | 69.9608 | 34.9804 | 15 | 35 | -0.019621 | -0.0093105 | 9.8532e-06 | -4.0986e-06 | -1 | 0
1020 | 17 | 5 | 12 | 5 | 12 | 69.9613 | 40 | -3.3668e-06 | 3.5433 | 6.4864e-06 | -4.6837e-05 | 4.7939 | 0 | 4.7938 |  | 15.1938 | 4 | 15.1938 | 69.9613 | 34.9806 | 15 | 35 | -0.019353 | -0.028664 | 3.3668e-06 | -4.054e-06 | -1 | 0
1021 | 17.0167 | 5 | 12 | 5 | 12 | 69.9619 | 40 | 3.0402e-06 | 3.5433 | 6.4069e-06 | 4.2293e-05 | 4.7939 | 0 | 4.7939 |  | 15.1939 | 4 | 15.1939 | 69.9619 | 34.9809 | 15 | 35 | -0.019062 | -0.047726 | 3.0402e-06 | -4.0043e-06 | -1 | 0
1022 | 17.0333 | 5 | 12 | 5 | 12 | 69.9625 | 40 | 9.3597e-06 | 3.5433 | 6.3195e-06 | 0.00013021 | 4.7939 | 0 | 4.794 |  | 15.194 | 4 | 15.194 | 69.9625 | 34.9813 | 15 | 35 | -0.018748 | -0.066474 | 9.3597e-06 | -3.9497e-06 | -1 | 0
1023 | 17.05 | 5 | 12 | 5 | 12 | 69.9632 | 40 | 1.5584e-05 | 3.5433 | 6.2244e-06 | 0.0002168 | 4.7939 | 0 | 4.7941 |  | 15.1941 | 4 | 15.1941 | 69.9632 | 34.9816 | 15 | 35 | -0.018411 | -0.084885 | 1.5584e-05 | -3.8902e-06 | -1 | 0
1024 | 17.0667 | 5 | 12 | 5 | 12 | 69.9639 | 40 | 2.1706e-05 | 3.5433 | 6.1217e-06 | 0.00030196 | 4.7939 | 0 | 4.7942 |  | 15.1942 | 4 | 15.1942 | 69.9639 | 34.9819 | 15 | 35 | -0.018053 | -0.10294 | 2.1706e-05 | -3.8261e-06 | -1 | 0
1025 | 17.0833 | 5 | 12 | 5 | 12 | 69.9647 | 40 | 2.7718e-05 | 3.5434 | 6.0118e-06 | 0.00038559 | 4.794 | 0 | 4.7943 |  | 15.1943 | 4 | 15.1943 | 69.9647 | 34.9823 | 15 | 35 | -0.017675 | -0.12061 | 2.7718e-05 | -3.7574e-06 | -1 | 0
1026 | 17.1 | 5 | 12 | 5 | 12 | 69.9654 | 40 | 3.3613e-05 | 3.5434 | 5.895e-06 | 0.0004676 | 4.794 | 0 | 4.7945 |  | 15.1945 | 4 | 15.1945 | 69.9654 | 34.9827 | 15 | 35 | -0.017276 | -0.13789 | 3.3613e-05 | -3.6844e-06 | -1 | 0
1027 | 17.1167 | 5 | 12 | 5 | 12 | 69.9663 | 40 | 3.9384e-05 | 3.5434 | 5.7714e-06 | 0.00054789 | 4.7941 | 0 | 4.7946 |  | 15.1946 | 4 | 15.1946 | 69.9663 | 34.9831 | 15 | 35 | -0.016859 | -0.15475 | 3.9384e-05 | -3.6071e-06 | -1 | 0
1028 | 17.1333 | 5 | 12 | 5 | 12 | 69.9672 | 40 | 4.5025e-05 | 3.5435 | 5.6413e-06 | 0.00062637 | 4.7941 | 0 | 4.7947 |  | 15.1947 | 4 | 15.1947 | 69.9672 | 34.9836 | 15 | 35 | -0.016423 | -0.17117 | 4.5025e-05 | -3.5258e-06 | -1 | 0
1029 | 17.15 | 5 | 11.9999 | 5 | 12 | 69.9681 | 40 | 5.053e-05 | 3.5435 | 5.505e-06 | 0.00070295 | 4.7942 | 0 | 4.7949 |  | 15.1949 | 4 | 15.1949 | 69.9681 | 34.984 | 15 | 35 | -0.01597 | -0.18714 | 5.053e-05 | -3.4406e-06 | -1 | 0
1030 | 17.1667 | 5 | 11.9999 | 5 | 12 | 69.969 | 40 | 5.5893e-05 | 3.5436 | 5.3628e-06 | 0.00077756 | 4.7943 | 0 | 4.795 |  | 15.195 | 4 | 15.195 | 69.969 | 34.9845 | 15 | 35 | -0.015501 | -0.20264 | 5.5893e-05 | -3.3517e-06 | -1 | 0
1031 | 17.1833 | 5 | 11.9999 | 5 | 12 | 69.97 | 40 | 6.1108e-05 | 3.5436 | 5.2148e-06 | 0.0008501 | 4.7943 | 0 | 4.7952 |  | 15.1952 | 4 | 15.1952 | 69.97 | 34.985 | 15 | 35 | -0.015016 | -0.21766 | 6.1108e-05 | -3.2593e-06 | -1 | 0
1032 | 17.2 | 5 | 11.9999 | 5 | 12 | 69.971 | 40 | 6.6169e-05 | 3.5437 | 5.0616e-06 | 0.00092052 | 4.7944 | 0 | 4.7954 |  | 15.1954 | 4 | 15.1954 | 69.971 | 34.9855 | 15 | 35 | -0.014516 | -0.23218 | 6.6169e-05 | -3.1635e-06 | -1 | 0
1033 | 17.2167 | 5 | 11.9999 | 5 | 12 | 69.972 | 40 | 7.1073e-05 | 3.5438 | 4.9032e-06 | 0.00098873 | 4.7945 | 0 | 4.7955 |  | 15.1955 | 4 | 15.1955 | 69.972 | 34.986 | 15 | 35 | -0.014002 | -0.24618 | 7.1073e-05 | -3.0645e-06 | -1 | 0
1034 | 17.2333 | 5 | 11.9999 | 5 | 12 | 69.973 | 40 | 7.5813e-05 | 3.5439 | 4.74e-06 | 0.0010547 | 4.7946 | 0 | 4.7957 |  | 15.1957 | 4 | 15.1957 | 69.973 | 34.9865 | 15 | 35 | -0.013476 | -0.25965 | 7.5813e-05 | -2.9625e-06 | -1 | 0
1035 | 17.25 | 4.9999 | 11.9999 | 5 | 12 | 69.9741 | 40 | 8.0385e-05 | 3.5439 | 4.5722e-06 | 0.0011183 | 4.7947 | 0 | 4.7959 |  | 15.1959 | 4 | 15.1959 | 69.9741 | 34.9871 | 15 | 35 | -0.012937 | -0.27259 | 8.0385e-05 | -2.8577e-06 | -1 | 0
1036 | 17.2667 | 4.9999 | 11.9999 | 5 | 12 | 69.9752 | 40 | 8.4785e-05 | 3.544 | 4.4003e-06 | 0.0011795 | 4.7949 | 0 | 4.796 |  | 15.196 | 4 | 15.196 | 69.9752 | 34.9876 | 15 | 35 | -0.012388 | -0.28498 | 8.4785e-05 | -2.7502e-06 | -1 | 0
1037 | 17.2833 | 4.9999 | 11.9999 | 5 | 12 | 69.9763 | 40 | 8.9009e-05 | 3.5441 | 4.2244e-06 | 0.0012383 | 4.795 | 0 | 4.7962 |  | 15.1962 | 4 | 15.1962 | 69.9763 | 34.9882 | 15 | 35 | -0.011828 | -0.29681 | 8.9009e-05 | -2.6403e-06 | -1 | 0
1038 | 17.3 | 4.9999 | 11.9999 | 5 | 12 | 69.9775 | 40 | 9.3054e-05 | 3.5442 | 4.0449e-06 | 0.0012945 | 4.7951 | 0 | 4.7964 |  | 15.1964 | 4 | 15.1964 | 69.9775 | 34.9887 | 15 | 35 | -0.011258 | -0.30806 | 9.3054e-05 | -2.5281e-06 | -1 | 0
1039 | 17.3167 | 4.9999 | 11.9999 | 5 | 12 | 69.9786 | 40 | 9.6916e-05 | 3.5443 | 3.862e-06 | 0.0013483 | 4.7952 | 0 | 4.7966 |  | 15.1966 | 4 | 15.1966 | 69.9786 | 34.9893 | 15 | 35 | -0.010681 | -0.31875 | 9.6916e-05 | -2.4138e-06 | -1 | 0
1040 | 17.3333 | 4.9999 | 11.9999 | 5 | 12 | 69.9798 | 40 | 0.00010059 | 3.5444 | 3.6762e-06 | 0.0013994 | 4.7954 | 0 | 4.7968 |  | 15.1968 | 4 | 15.1968 | 69.9798 | 34.9899 | 15 | 35 | -0.010095 | -0.32884 | 0.00010059 | -2.2976e-06 | -1 | 0
1041 | 17.35 | 4.9999 | 11.9999 | 5 | 12 | 69.981 | 40 | 0.00010408 | 3.5445 | 3.4875e-06 | 0.0014479 | 4.7955 | 0 | 4.797 |  | 15.197 | 4 | 15.197 | 69.981 | 34.9905 | 15 | 35 | -0.0095038 | -0.33834 | 0.00010408 | -2.1797e-06 | -1 | 0
1042 | 17.3667 | 4.9999 | 11.9999 | 5 | 12 | 69.9822 | 40 | 0.00010738 | 3.5446 | 3.2965e-06 | 0.0014938 | 4.7957 | 0 | 4.7971 |  | 15.1971 | 4 | 15.1971 | 69.9822 | 34.9911 | 15 | 35 | -0.0089065 | -0.34725 | 0.00010738 | -2.0603e-06 | -1 | 0
1043 | 17.3833 | 4.9999 | 11.9999 | 5 | 12 | 69.9834 | 40 | 0.00011048 | 3.5447 | 3.1033e-06 | 0.0015369 | 4.7958 | 0 | 4.7973 |  | 15.1973 | 4 | 15.1973 | 69.9834 | 34.9917 | 15 | 35 | -0.0083045 | -0.35556 | 0.00011048 | -1.9396e-06 | -1 | 0
1044 | 17.4 | 4.9999 | 11.9999 | 5 | 12 | 69.9846 | 40 | 0.00011339 | 3.5448 | 2.9083e-06 | 0.0015774 | 4.796 | 0 | 4.7975 |  | 15.1975 | 4 | 15.1975 | 69.9846 | 34.9923 | 15 | 35 | -0.0076987 | -0.36325 | 0.00011339 | -1.8177e-06 | -1 | 0
1045 | 17.4167 | 4.9999 | 11.9999 | 5 | 12 | 69.9858 | 40 | 0.0001161 | 3.545 | 2.7117e-06 | 0.0016151 | 4.7961 | 0 | 4.7977 |  | 15.1977 | 4 | 15.1977 | 69.9858 | 34.9929 | 15 | 35 | -0.0070899 | -0.37034 | 0.0001161 | -1.6948e-06 | -1 | 0
1046 | 17.4333 | 4.9999 | 11.9999 | 5 | 12 | 69.987 | 40 | 0.00011861 | 3.5451 | 2.5139e-06 | 0.0016501 | 4.7963 | 0 | 4.7979 |  | 15.1979 | 4 | 15.1979 | 69.987 | 34.9935 | 15 | 35 | -0.0064792 | -0.37682 | 0.00011861 | -1.5712e-06 | -1 | 0
1047 | 17.45 | 4.9999 | 11.9999 | 5 | 12 | 69.9883 | 40 | 0.00012093 | 3.5452 | 2.3151e-06 | 0.0016823 | 4.7964 | 0 | 4.7981 |  | 15.1981 | 4 | 15.1981 | 69.9883 | 34.9941 | 15 | 35 | -0.0058672 | -0.38269 | 0.00012093 | -1.4469e-06 | -1 | 0
1048 | 17.4667 | 4.9999 | 11.9999 | 5 | 12 | 69.9895 | 40 | 0.00012304 | 3.5453 | 2.1156e-06 | 0.0017117 | 4.7966 | 0 | 4.7983 |  | 15.1983 | 4 | 15.1983 | 69.9895 | 34.9947 | 15 | 35 | -0.005255 | -0.38795 | 0.00012304 | -1.3223e-06 | -1 | 0
1049 | 17.4833 | 4.9999 | 11.9999 | 5 | 12 | 69.9907 | 40 | 0.00012496 | 3.5454 | 1.9158e-06 | 0.0017384 | 4.7968 | 0 | 4.7985 |  | 15.1985 | 4 | 15.1985 | 69.9907 | 34.9954 | 15 | 35 | -0.0046434 | -0.39259 | 0.00012496 | -1.1974e-06 | -1 | 0
1050 | 17.5 | 4.9999 | 11.9999 | 5 | 12 | 69.9919 | 40 | 0.00012668 | 3.5456 | 1.7159e-06 | 0.0017623 | 4.7969 | 0 | 4.7987 |  | 15.1987 | 4 | 15.1987 | 69.9919 | 34.996 | 15 | 35 | -0.0040332 | -0.39662 | 0.00012668 | -1.0725e-06 | -1 | 0
1051 | 17.5167 | 4.9999 | 11.9999 | 5 | 12 | 69.9931 | 40 | 0.00012819 | 3.5457 | 1.5162e-06 | 0.0017834 | 4.7971 | 0 | 4.7989 |  | 15.1989 | 4 | 15.1989 | 69.9931 | 34.9966 | 15 | 35 | -0.0034253 | -0.40005 | 0.00012819 | -9.4764e-07 | -1 | 0
1052 | 17.5333 | 4.9999 | 11.9999 | 5 | 12 | 69.9944 | 40 | 0.00012951 | 3.5458 | 1.317e-06 | 0.0018017 | 4.7973 | 0 | 4.7991 |  | 15.1991 | 4 | 15.1991 | 69.9944 | 34.9972 | 15 | 35 | -0.0028205 | -0.40287 | 0.00012951 | -8.2311e-07 | -1 | 0
1053 | 17.55 | 4.9999 | 11.9999 | 5 | 12 | 69.9956 | 40 | 0.00013063 | 3.546 | 1.1185e-06 | 0.0018172 | 4.7975 | 0 | 4.7993 |  | 15.1993 | 4 | 15.1993 | 69.9956 | 34.9978 | 15 | 35 | -0.0022196 | -0.40509 | 0.00013063 | -6.9905e-07 | -1 | 0
1054 | 17.5667 | 4.9999 | 11.9999 | 5 | 12 | 69.9968 | 40 | 0.00013155 | 3.5461 | 9.2099e-07 | 0.00183 | 4.7977 | 0 | 4.7995 |  | 15.1995 | 4 | 15.1995 | 69.9968 | 34.9984 | 15 | 35 | -0.0016234 | -0.40671 | 0.00013155 | -5.7562e-07 | -1 | 0
1055 | 17.5833 | 4.9999 | 11.9999 | 5 | 12 | 69.9979 | 40 | 0.00013227 | 3.5462 | 7.2477e-07 | 0.0018401 | 4.7978 | 0 | 4.7997 |  | 15.1997 | 4 | 15.1997 | 69.9979 | 34.999 | 15 | 35 | -0.0010326 | -0.40774 | 0.00013227 | -4.5298e-07 | -1 | 0
1056 | 17.6 | 4.9999 | 11.9999 | 5 | 12 | 69.9991 | 40 | 0.0001328 | 3.5464 | 5.3009e-07 | 0.0018475 | 4.798 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9991 | 34.9996 | 15 | 35 | -0.00044811 | -0.40819 | 0.0001328 | -3.3131e-07 | -1 | 0
1057 | 17.6167 | 4.9999 | 11.9999 | 5 | 12 | 70.0003 | 40 | 0.00013314 | 3.5465 | 3.3719e-07 | 0.0018522 | 4.7982 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0003 | 35.0001 | 15 | 35 | 0.00012946 | -0.40806 | 0.00013314 | -2.1074e-07 | -1 | 0
1058 | 17.6333 | 4.9999 | 11.9999 | 5 | 12 | 70.0014 | 40 | 0.00013329 | 3.5466 | 1.4632e-07 | 0.0018542 | 4.7984 | 0 | 4.8002 |  | 15.2002 | 4 | 15.2002 | 70.0014 | 35.0007 | 15 | 35 | 0.00069935 | -0.40736 | 0.00013329 | -9.1451e-08 | -1 | 0
1059 | 17.65 | 4.9999 | 11.9999 | 5 | 12 | 70.0025 | 40 | 0.00013324 | 3.5468 | -4.2273e-08 | 0.0018536 | 4.7985 | 0 | 4.8004 |  | 15.2004 | 4 | 15.2004 | 70.0025 | 35.0013 | 15 | 35 | 0.0012609 | -0.4061 | 0.00013324 | 2.642e-08 | 1 | 2
1060 | 17.6667 | 4.9999 | 11.9999 | 5 | 12 | 70.0036 | 40 | 0.00013302 | 3.5469 | -2.2836e-07 | 0.0018505 | 4.7987 | 0 | 4.8006 |  | 15.2006 | 4 | 15.2006 | 70.0036 | 35.0018 | 15 | 35 | 0.0018133 | -0.40429 | 0.00013302 | 1.4272e-07 | 1 | 0
1061 | 17.6833 | 4.9999 | 11.9999 | 5 | 12 | 70.0047 | 40 | 0.0001326 | 3.547 | -4.1171e-07 | 0.0018447 | 4.7989 | 0 | 4.8008 |  | 15.2008 | 4 | 15.2008 | 70.0047 | 35.0024 | 15 | 35 | 0.0023561 | -0.40193 | 0.0001326 | 2.5732e-07 | 1 | 0
1062 | 17.7 | 4.9999 | 11.9999 | 5 | 12 | 70.0058 | 40 | 0.00013201 | 3.5472 | -5.9211e-07 | 0.0018365 | 4.7991 | 0 | 4.8009 |  | 15.2009 | 4 | 15.2009 | 70.0058 | 35.0029 | 15 | 35 | 0.0028885 | -0.39904 | 0.00013201 | 3.7007e-07 | 1 | 0
1063 | 17.7167 | 4.9999 | 11.9999 | 5 | 12 | 70.0068 | 40 | 0.00013124 | 3.5473 | -7.6933e-07 | 0.0018258 | 4.7993 | 0 | 4.8011 |  | 15.2011 | 4 | 15.2011 | 70.0068 | 35.0034 | 15 | 35 | 0.0034099 | -0.39563 | 0.00013124 | 4.8083e-07 | 1 | 0
1064 | 17.7333 | 4.9999 | 11.9999 | 5 | 12 | 70.0078 | 40 | 0.0001303 | 3.5474 | -9.4317e-07 | 0.0018127 | 4.7994 | 0 | 4.8013 |  | 15.2013 | 4 | 15.2013 | 70.0078 | 35.0039 | 15 | 35 | 0.0039198 | -0.39171 | 0.0001303 | 5.8948e-07 | 1 | 0
1065 | 17.75 | 4.9999 | 11.9999 | 5 | 12 | 70.0088 | 40 | 0.00012919 | 3.5475 | -1.1134e-06 | 0.0017972 | 4.7996 | 0 | 4.8014 |  | 15.2014 | 4 | 15.2014 | 70.0088 | 35.0044 | 15 | 35 | 0.0044176 | -0.3873 | 0.00012919 | 6.959e-07 | 1 | 0
1066 | 17.7667 | 4.9999 | 11.9999 | 5 | 12 | 70.0098 | 40 | 0.00012791 | 3.5477 | -1.2799e-06 | 0.0017794 | 4.7998 | 0 | 4.8016 |  | 15.2016 | 4 | 15.2016 | 70.0098 | 35.0049 | 15 | 35 | 0.0049027 | -0.38239 | 0.00012791 | 7.9996e-07 | 1 | 0
1067 | 17.7833 | 4.9999 | 11.9999 | 5 | 12 | 70.0107 | 40 | 0.00012646 | 3.5478 | -1.4425e-06 | 0.0017593 | 4.8 | 0 | 4.8017 |  | 15.2017 | 4 | 15.2017 | 70.0107 | 35.0054 | 15 | 35 | 0.0053747 | -0.37702 | 0.00012646 | 9.0155e-07 | 1 | 0
1068 | 17.8 | 4.9999 | 11.9999 | 5 | 12 | 70.0117 | 40 | 0.00012486 | 3.5479 | -1.6009e-06 | 0.001737 | 4.8001 | 0 | 4.8019 |  | 15.2019 | 4 | 15.2019 | 70.0117 | 35.0058 | 15 | 35 | 0.005833 | -0.37119 | 0.00012486 | 1.0006e-06 | 1 | 0
1069 | 17.8167 | 4.9999 | 11.9999 | 5 | 12 | 70.0126 | 40 | 0.00012311 | 3.548 | -1.755e-06 | 0.0017126 | 4.8003 | 0 | 4.802 |  | 15.202 | 4 | 15.202 | 70.0126 | 35.0063 | 15 | 35 | 0.0062772 | -0.36491 | 0.00012311 | 1.0969e-06 | 1 | 0
1070 | 17.8333 | 4.9999 | 11.9999 | 5 | 12 | 70.0134 | 40 | 0.0001212 | 3.5482 | -1.9047e-06 | 0.0016861 | 4.8005 | 0 | 4.8021 |  | 15.2021 | 4 | 15.2021 | 70.0134 | 35.0067 | 15 | 35 | 0.0067069 | -0.3582 | 0.0001212 | 1.1904e-06 | 1 | 0
1071 | 17.85 | 4.9999 | 11.9999 | 5 | 12 | 70.0142 | 40 | 0.00011915 | 3.5483 | -2.0497e-06 | 0.0016576 | 4.8006 | 0 | 4.8023 |  | 15.2023 | 4 | 15.2023 | 70.0142 | 35.0071 | 15 | 35 | 0.0071215 | -0.35108 | 0.00011915 | 1.2811e-06 | 1 | 0
1072 | 17.8667 | 4.9999 | 11.9999 | 5 | 12 | 70.015 | 40 | 0.00011696 | 3.5484 | -2.19e-06 | 0.0016272 | 4.8008 | 0 | 4.8024 |  | 15.2024 | 4 | 15.2024 | 70.015 | 35.0075 | 15 | 35 | 0.0075209 | -0.34356 | 0.00011696 | 1.3687e-06 | 1 | 0
1073 | 17.8833 | 4.9999 | 11.9999 | 5 | 12 | 70.0158 | 40 | 0.00011464 | 3.5485 | -2.3254e-06 | 0.0015948 | 4.8009 | 0 | 4.8025 |  | 15.2025 | 4 | 15.2025 | 70.0158 | 35.0079 | 15 | 35 | 0.0079044 | -0.33566 | 0.00011464 | 1.4534e-06 | 1 | 0
1074 | 17.9 | 4.9999 | 11.9999 | 5 | 12 | 70.0165 | 40 | 0.00011218 | 3.5486 | -2.4558e-06 | 0.0015606 | 4.8011 | 0 | 4.8026 |  | 15.2026 | 4 | 15.2026 | 70.0165 | 35.0083 | 15 | 35 | 0.008272 | -0.32738 | 0.00011218 | 1.5349e-06 | 1 | 0
1075 | 17.9167 | 4.9999 | 11.9999 | 5 | 12 | 70.0172 | 40 | 0.0001096 | 3.5487 | -2.581e-06 | 0.0015247 | 4.8012 | 0 | 4.8028 |  | 15.2028 | 4 | 15.2028 | 70.0172 | 35.0086 | 15 | 35 | 0.0086232 | -0.31876 | 0.0001096 | 1.6132e-06 | 1 | 0
1076 | 17.9333 | 4.9999 | 11.9999 | 5 | 12 | 70.0179 | 40 | 0.0001069 | 3.5488 | -2.7011e-06 | 0.0014872 | 4.8014 | 0 | 4.8029 |  | 15.2029 | 4 | 15.2029 | 70.0179 | 35.009 | 15 | 35 | 0.0089577 | -0.3098 | 0.0001069 | 1.6882e-06 | 1 | 0
1077 | 17.95 | 4.9999 | 11.9999 | 5 | 12 | 70.0186 | 40 | 0.00010409 | 3.5489 | -2.8157e-06 | 0.001448 | 4.8015 | 0 | 4.803 |  | 15.203 | 4 | 15.203 | 70.0186 | 35.0093 | 15 | 35 | 0.0092754 | -0.30053 | 0.00010409 | 1.7598e-06 | 1 | 0
1078 | 17.9667 | 4.9999 | 11.9999 | 5 | 12 | 70.0192 | 40 | 0.00010116 | 3.5491 | -2.925e-06 | 0.0014073 | 4.8017 | 0 | 4.8031 |  | 15.2031 | 4 | 15.2031 | 70.0192 | 35.0096 | 15 | 35 | 0.0095759 | -0.29095 | 0.00010116 | 1.8281e-06 | 1 | 0
1079 | 17.9833 | 4.9999 | 11.9999 | 5 | 12 | 70.0197 | 40 | 9.8131e-05 | 3.5491 | -3.0287e-06 | 0.0013652 | 4.8018 | 0 | 4.8032 |  | 15.2032 | 4 | 15.2032 | 70.0197 | 35.0099 | 15 | 35 | 0.0098591 | -0.28109 | 9.8131e-05 | 1.8929e-06 | 1 | 0
1080 | 18 | 4.9999 | 11.9999 | 5 | 12 | 70.0202 | 40 | 9.5005e-05 | 3.5492 | -3.1268e-06 | 0.0013217 | 4.8019 | 0 | 4.8032 |  | 15.2032 | 4 | 15.2032 | 70.0202 | 35.0101 | 15 | 35 | 0.010125 | -0.27097 | 9.5005e-05 | 1.9543e-06 | 1 | 0
1081 | 18.0167 | 4.9999 | 11.9999 | 5 | 12 | 70.0207 | 40 | 9.1785e-05 | 3.5493 | -3.2193e-06 | 0.0012769 | 4.802 | 0 | 4.8033 |  | 15.2033 | 4 | 15.2033 | 70.0207 | 35.0104 | 15 | 35 | 0.010373 | -0.26059 | 9.1785e-05 | 2.0121e-06 | 1 | 0
1082 | 18.0333 | 4.9999 | 11.9999 | 5 | 12 | 70.0212 | 40 | 8.8479e-05 | 3.5494 | -3.3061e-06 | 0.0012309 | 4.8022 | 0 | 4.8034 |  | 15.2034 | 4 | 15.2034 | 70.0212 | 35.0106 | 15 | 35 | 0.010603 | -0.24999 | 8.8479e-05 | 2.0663e-06 | 1 | 0
1083 | 18.05 | 4.9999 | 11.9999 | 5 | 12 | 70.0216 | 40 | 8.5092e-05 | 3.5495 | -3.3871e-06 | 0.0011838 | 4.8023 | 0 | 4.8035 |  | 15.2035 | 4 | 15.2035 | 70.0216 | 35.0108 | 15 | 35 | 0.010816 | -0.23918 | 8.5092e-05 | 2.1169e-06 | 1 | 0
1084 | 18.0667 | 4.9999 | 11.9999 | 5 | 12 | 70.022 | 40 | 8.163e-05 | 3.5496 | -3.4623e-06 | 0.0011356 | 4.8024 | 0 | 4.8035 |  | 15.2035 | 4 | 15.2035 | 70.022 | 35.011 | 15 | 35 | 0.01101 | -0.22816 | 8.163e-05 | 2.1639e-06 | 1 | 0
1085 | 18.0833 | 5 | 11.9999 | 5 | 12 | 70.0224 | 40 | 7.8098e-05 | 3.5497 | -3.5317e-06 | 0.0010865 | 4.8025 | 0 | 4.8036 |  | 15.2036 | 4 | 15.2036 | 70.0224 | 35.0112 | 15 | 35 | 0.011187 | -0.21698 | 7.8098e-05 | 2.2073e-06 | 1 | 0
1086 | 18.1 | 5 | 11.9999 | 5 | 12 | 70.0227 | 40 | 7.4503e-05 | 3.5497 | -3.5953e-06 | 0.0010365 | 4.8026 | 0 | 4.8036 |  | 15.2036 | 4 | 15.2036 | 70.0227 | 35.0113 | 15 | 35 | 0.011346 | -0.20563 | 7.4503e-05 | 2.247e-06 | 1 | 0
1087 | 18.1167 | 5 | 11.9999 | 5 | 12 | 70.023 | 40 | 7.085e-05 | 3.5498 | -3.6529e-06 | 0.00098563 | 4.8027 | 0 | 4.8037 |  | 15.2037 | 4 | 15.2037 | 70.023 | 35.0115 | 15 | 35 | 0.011487 | -0.19415 | 7.085e-05 | 2.2831e-06 | 1 | 0
1088 | 18.1333 | 5 | 11.9999 | 5 | 12 | 70.0232 | 40 | 6.7145e-05 | 3.5499 | -3.7048e-06 | 0.00093409 | 4.8028 | 0 | 4.8037 |  | 15.2037 | 4 | 15.2037 | 70.0232 | 35.0116 | 15 | 35 | 0.011609 | -0.18254 | 6.7145e-05 | 2.3155e-06 | 1 | 0
1089 | 18.15 | 5 | 11.9999 | 5 | 12 | 70.0234 | 40 | 6.3394e-05 | 3.5499 | -3.7507e-06 | 0.00088192 | 4.8029 | 0 | 4.8037 |  | 15.2037 | 4 | 15.2037 | 70.0234 | 35.0117 | 15 | 35 | 0.011714 | -0.17082 | 6.3394e-05 | 2.3442e-06 | 1 | 0
1090 | 18.1667 | 5 | 11.9999 | 5 | 12 | 70.0236 | 40 | 5.9604e-05 | 3.55 | -3.7908e-06 | 0.00082918 | 4.8029 | 0 | 4.8038 |  | 15.2038 | 4 | 15.2038 | 70.0236 | 35.0118 | 15 | 35 | 0.011802 | -0.15902 | 5.9604e-05 | 2.3693e-06 | 1 | 0
1091 | 18.1833 | 5 | 11.9999 | 5 | 12 | 70.0237 | 40 | 5.5779e-05 | 3.5501 | -3.8251e-06 | 0.00077597 | 4.803 | 0 | 4.8038 |  | 15.2038 | 4 | 15.2038 | 70.0237 | 35.0119 | 15 | 35 | 0.011871 | -0.14715 | 5.5779e-05 | 2.3907e-06 | 1 | 0
1092 | 18.2 | 5 | 11.9999 | 5 | 12 | 70.0238 | 40 | 5.1925e-05 | 3.5501 | -3.8536e-06 | 0.00072236 | 4.8031 | 0 | 4.8038 |  | 15.2038 | 4 | 15.2038 | 70.0238 | 35.0119 | 15 | 35 | 0.011923 | -0.13523 | 5.1925e-05 | 2.4085e-06 | 1 | 0
1093 | 18.2167 | 5 | 12 | 5 | 12 | 70.0239 | 40 | 4.8049e-05 | 3.5502 | -3.8763e-06 | 0.00066843 | 4.8032 | 0 | 4.8038 |  | 15.2038 | 4 | 15.2038 | 70.0239 | 35.012 | 15 | 35 | 0.011958 | -0.12327 | 4.8049e-05 | 2.4227e-06 | 1 | 0
1094 | 18.2333 | 5 | 12 | 5 | 12 | 70.024 | 40 | 4.4155e-05 | 3.5502 | -3.8933e-06 | 0.00061427 | 4.8032 | 0 | 4.8038 |  | 15.2038 | 4 | 15.2038 | 70.024 | 35.012 | 15 | 35 | 0.011975 | -0.11129 | 4.4155e-05 | 2.4333e-06 | 1 | 0
1095 | 18.25 | 5 | 12 | 5 | 12 | 70.024 | 40 | 4.0251e-05 | 3.5502 | -3.9046e-06 | 0.00055995 | 4.8033 | 0 | 4.8038 |  | 15.2038 | 4 | 15.2038 | 70.024 | 35.012 | 15 | 35 | 0.011976 | -0.099317 | 4.0251e-05 | 2.4404e-06 | 1 | 0
1096 | 18.2667 | 5 | 12 | 5 | 12 | 70.0239 | 40 | 3.6341e-05 | 3.5503 | -3.9103e-06 | 0.00050555 | 4.8033 | 0 | 4.8038 |  | 15.2038 | 4 | 15.2038 | 70.0239 | 35.012 | 15 | 35 | 0.011959 | -0.087358 | 3.6341e-05 | 2.4439e-06 | 1 | 0
1097 | 18.2833 | 5 | 12 | 5 | 12 | 70.0239 | 40 | 3.243e-05 | 3.5503 | -3.9104e-06 | 0.00045115 | 4.8034 | 0 | 4.8038 |  | 15.2038 | 4 | 15.2038 | 70.0239 | 35.0119 | 15 | 35 | 0.011926 | -0.075432 | 3.243e-05 | 2.444e-06 | 1 | 0
1098 | 18.3 | 5 | 12 | 5 | 12 | 70.0238 | 40 | 2.8525e-05 | 3.5503 | -3.9051e-06 | 0.00039683 | 4.8034 | 0 | 4.8038 |  | 15.2038 | 4 | 15.2038 | 70.0238 | 35.0119 | 15 | 35 | 0.011877 | -0.063555 | 2.8525e-05 | 2.4407e-06 | 1 | 0
1099 | 18.3167 | 5 | 12 | 5 | 12 | 70.0236 | 40 | 2.4631e-05 | 3.5504 | -3.8943e-06 | 0.00034265 | 4.8034 | 0 | 4.8038 |  | 15.2038 | 4 | 15.2038 | 70.0236 | 35.0118 | 15 | 35 | 0.011812 | -0.051743 | 2.4631e-05 | 2.434e-06 | 1 | 0
1100 | 18.3333 | 5 | 12 | 5 | 12 | 70.0235 | 40 | 2.0753e-05 | 3.5504 | -3.8783e-06 | 0.0002887 | 4.8035 | 0 | 4.8038 |  | 15.2038 | 4 | 15.2038 | 70.0235 | 35.0117 | 15 | 35 | 0.011731 | -0.040011 | 2.0753e-05 | 2.4239e-06 | 1 | 0
1101 | 18.35 | 5 | 12 | 5 | 12 | 70.0233 | 40 | 1.6896e-05 | 3.5504 | -3.857e-06 | 0.00023504 | 4.8035 | 0 | 4.8037 |  | 15.2037 | 4 | 15.2037 | 70.0233 | 35.0116 | 15 | 35 | 0.011635 | -0.028377 | 1.6896e-05 | 2.4106e-06 | 1 | 0
1102 | 18.3667 | 5 | 12 | 5 | 12 | 70.023 | 40 | 1.3065e-05 | 3.5504 | -3.8306e-06 | 0.00018175 | 4.8035 | 0 | 4.8037 |  | 15.2037 | 4 | 15.2037 | 70.023 | 35.0115 | 15 | 35 | 0.011524 | -0.016853 | 1.3065e-05 | 2.3941e-06 | 1 | 0
1103 | 18.3833 | 5 | 12 | 5 | 12 | 70.0228 | 40 | 9.2658e-06 | 3.5504 | -3.7992e-06 | 0.0001289 | 4.8035 | 0 | 4.8036 |  | 15.2036 | 4 | 15.2036 | 70.0228 | 35.0114 | 15 | 35 | 0.011398 | -0.0054552 | 9.2658e-06 | 2.3745e-06 | 1 | 0
1104 | 18.4 | 5 | 12 | 5 | 12 | 70.0225 | 40 | 5.503e-06 | 3.5504 | -3.7628e-06 | 7.6555e-05 | 4.8035 | 0 | 4.8036 |  | 15.2036 | 4 | 15.2036 | 70.0225 | 35.0113 | 15 | 35 | 0.011257 | 0.0058021 | 5.503e-06 | 2.3518e-06 | 1 | 0
1105 | 18.4167 | 5 | 12 | 5 | 12 | 70.0222 | 40 | 1.7813e-06 | 3.5504 | -3.7217e-06 | 2.4781e-05 | 4.8035 | 0 | 4.8036 |  | 15.2036 | 4 | 15.2036 | 70.0222 | 35.0111 | 15 | 35 | 0.011103 | 0.016905 | 1.7813e-06 | 2.3261e-06 | 1 | 0
1106 | 18.4333 | 5 | 12 | 5 | 12 | 70.0219 | 40 | -1.8946e-06 | 3.5504 | -3.6759e-06 | -2.6356e-05 | 4.8035 | 0 | 4.8035 |  | 15.2035 | 4 | 15.2035 | 70.0219 | 35.0109 | 15 | 35 | 0.010935 | 0.02784 | 1.8946e-06 | 2.2974e-06 | 1 | 0
1107 | 18.45 | 5 | 12 | 5 | 12 | 70.0215 | 40 | -5.5201e-06 | 3.5504 | -3.6255e-06 | -7.6793e-05 | 4.8035 | 0 | 4.8034 |  | 15.2034 | 4 | 15.2034 | 70.0215 | 35.0108 | 15 | 35 | 0.010754 | 0.038595 | 5.5201e-06 | 2.2659e-06 | 1 | 0
1108 | 18.4667 | 5 | 12 | 5 | 12 | 70.0211 | 40 | -9.0908e-06 | 3.5504 | -3.5707e-06 | -0.00012647 | 4.8035 | 0 | 4.8034 |  | 15.2034 | 4 | 15.2034 | 70.0211 | 35.0106 | 15 | 35 | 0.010561 | 0.049155 | 9.0908e-06 | 2.2317e-06 | 1 | 0
1109 | 18.4833 | 5 | 12 | 5 | 12 | 70.0207 | 40 | -1.2602e-05 | 3.5504 | -3.5116e-06 | -0.00017532 | 4.8035 | 0 | 4.8033 |  | 15.2033 | 4 | 15.2033 | 70.0207 | 35.0104 | 15 | 35 | 0.010355 | 0.05951 | 1.2602e-05 | 2.1948e-06 | 1 | 0
1110 | 18.5 | 5 | 12 | 5 | 12 | 70.0203 | 40 | -1.6051e-05 | 3.5504 | -3.4484e-06 | -0.00022329 | 4.8035 | 0 | 4.8032 |  | 15.2032 | 4 | 15.2032 | 70.0203 | 35.0101 | 15 | 35 | 0.010137 | 0.069647 | 1.6051e-05 | 2.1552e-06 | 1 | 0
1111 | 18.5167 | 5 | 12 | 5 | 12 | 70.0198 | 40 | -1.9432e-05 | 3.5504 | -3.3811e-06 | -0.00027033 | 4.8034 | 0 | 4.8032 |  | 15.2032 | 4 | 15.2032 | 70.0198 | 35.0099 | 15 | 35 | 0.0099078 | 0.079555 | 1.9432e-05 | 2.1132e-06 | 1 | 0
1112 | 18.5333 | 5 | 12 | 5 | 12 | 70.0193 | 40 | -2.2742e-05 | 3.5503 | -3.31e-06 | -0.00031637 | 4.8034 | 0 | 4.8031 |  | 15.2031 | 4 | 15.2031 | 70.0193 | 35.0097 | 15 | 35 | 0.0096677 | 0.089222 | 2.2742e-05 | 2.0688e-06 | 1 | 0
1113 | 18.55 | 5 | 12 | 5 | 12 | 70.0188 | 40 | -2.5977e-05 | 3.5503 | -3.2352e-06 | -0.00036138 | 4.8034 | 0 | 4.803 |  | 15.203 | 4 | 15.203 | 70.0188 | 35.0094 | 15 | 35 | 0.0094172 | 0.09864 | 2.5977e-05 | 2.022e-06 | 1 | 0
1114 | 18.5667 | 5 | 12 | 5 | 12 | 70.0183 | 40 | -2.9134e-05 | 3.5503 | -3.1568e-06 | -0.0004053 | 4.8033 | 0 | 4.8029 |  | 15.2029 | 4 | 15.2029 | 70.0183 | 35.0092 | 15 | 35 | 0.0091568 | 0.1078 | 2.9134e-05 | 1.973e-06 | 1 | 0
1115 | 18.5833 | 5 | 12 | 5 | 12 | 70.0178 | 40 | -3.2209e-05 | 3.5503 | -3.075e-06 | -0.00044808 | 4.8033 | 0 | 4.8028 |  | 15.2028 | 4 | 15.2028 | 70.0178 | 35.0089 | 15 | 35 | 0.008887 | 0.11668 | 3.2209e-05 | 1.9219e-06 | 1 | 0
1116 | 18.6 | 5 | 12 | 5 | 12 | 70.0172 | 40 | -3.5199e-05 | 3.5502 | -2.99e-06 | -0.00048967 | 4.8032 | 0 | 4.8028 |  | 15.2028 | 4 | 15.2028 | 70.0172 | 35.0086 | 15 | 35 | 0.0086082 | 0.12529 | 3.5199e-05 | 1.8687e-06 | 1 | 0
1117 | 18.6167 | 5 | 12 | 5 | 12 | 70.0166 | 40 | -3.8101e-05 | 3.5502 | -2.9019e-06 | -0.00053004 | 4.8032 | 0 | 4.8027 |  | 15.2027 | 4 | 15.2027 | 70.0166 | 35.0083 | 15 | 35 | 0.0083209 | 0.13361 | 3.8101e-05 | 1.8137e-06 | 1 | 0
1118 | 18.6333 | 5 | 12 | 5 | 12 | 70.0161 | 40 | -4.0912e-05 | 3.5501 | -2.8108e-06 | -0.00056914 | 4.8031 | 0 | 4.8026 |  | 15.2026 | 4 | 15.2026 | 70.0161 | 35.008 | 15 | 35 | 0.0080258 | 0.14164 | 4.0912e-05 | 1.7568e-06 | 1 | 0
1119 | 18.65 | 5 | 12 | 5 | 12 | 70.0154 | 40 | -4.3629e-05 | 3.5501 | -2.717e-06 | -0.00060694 | 4.8031 | 0 | 4.8025 |  | 15.2025 | 4 | 15.2025 | 70.0154 | 35.0077 | 15 | 35 | 0.0077232 | 0.14936 | 4.3629e-05 | 1.6981e-06 | 1 | 0
1120 | 18.6667 | 5 | 12 | 5 | 12 | 70.0148 | 40 | -4.6249e-05 | 3.5501 | -2.6207e-06 | -0.0006434 | 4.803 | 0 | 4.8024 |  | 15.2024 | 4 | 15.2024 | 70.0148 | 35.0074 | 15 | 35 | 0.0074137 | 0.15678 | 4.6249e-05 | 1.6379e-06 | 1 | 0
1121 | 18.6833 | 5 | 12 | 5 | 12 | 70.0142 | 40 | -4.8771e-05 | 3.55 | -2.5219e-06 | -0.00067848 | 4.8029 | 0 | 4.8023 |  | 15.2023 | 4 | 15.2023 | 70.0142 | 35.0071 | 15 | 35 | 0.0070979 | 0.16387 | 4.8771e-05 | 1.5762e-06 | 1 | 0
1122 | 18.7 | 5 | 12.0001 | 5 | 12 | 70.0136 | 40 | -5.1192e-05 | 3.55 | -2.4208e-06 | -0.00071216 | 4.8029 | 0 | 4.8022 |  | 15.2022 | 4 | 15.2022 | 70.0136 | 35.0068 | 15 | 35 | 0.0067762 | 0.17065 | 5.1192e-05 | 1.513e-06 | 1 | 0
1123 | 18.7167 | 5 | 12.0001 | 5 | 12 | 70.0129 | 40 | -5.351e-05 | 3.5499 | -2.3177e-06 | -0.0007444 | 4.8028 | 0 | 4.8021 |  | 15.2021 | 4 | 15.2021 | 70.0129 | 35.0064 | 15 | 35 | 0.0064492 | 0.1771 | 5.351e-05 | 1.4485e-06 | 1 | 0
1124 | 18.7333 | 5 | 12.0001 | 5 | 12 | 70.0122 | 40 | -5.5722e-05 | 3.5498 | -2.2126e-06 | -0.00077518 | 4.8027 | 0 | 4.802 |  | 15.202 | 4 | 15.202 | 70.0122 | 35.0061 | 15 | 35 | 0.0061174 | 0.18322 | 5.5722e-05 | 1.3829e-06 | 1 | 0
1125 | 18.75 | 5 | 12.0001 | 5 | 12 | 70.0116 | 40 | -5.7828e-05 | 3.5498 | -2.1059e-06 | -0.00080448 | 4.8027 | 0 | 4.8019 |  | 15.2019 | 4 | 15.2019 | 70.0116 | 35.0058 | 15 | 35 | 0.0057814 | 0.189 | 5.7828e-05 | 1.3162e-06 | 1 | 0
1126 | 18.7667 | 5 | 12.0001 | 5 | 12 | 70.0109 | 40 | -5.9826e-05 | 3.5497 | -1.9975e-06 | -0.00083227 | 4.8026 | 0 | 4.8017 |  | 15.2017 | 4 | 15.2017 | 70.0109 | 35.0054 | 15 | 35 | 0.0054416 | 0.19444 | 5.9826e-05 | 1.2485e-06 | 1 | 0
1127 | 18.7833 | 5 | 12.0001 | 5 | 12 | 70.0102 | 40 | -6.1713e-05 | 3.5497 | -1.8878e-06 | -0.00085853 | 4.8025 | 0 | 4.8016 |  | 15.2016 | 4 | 15.2016 | 70.0102 | 35.0051 | 15 | 35 | 0.0050986 | 0.19954 | 6.1713e-05 | 1.1799e-06 | 1 | 0
1128 | 18.8 | 5 | 12.0001 | 5 | 12 | 70.0095 | 40 | -6.349e-05 | 3.5496 | -1.7768e-06 | -0.00088325 | 4.8024 | 0 | 4.8015 |  | 15.2015 | 4 | 15.2015 | 70.0095 | 35.0048 | 15 | 35 | 0.0047529 | 0.20429 | 6.349e-05 | 1.1105e-06 | 1 | 0
1129 | 18.8167 | 5 | 12.0001 | 5 | 12 | 70.0088 | 40 | -6.5155e-05 | 3.5495 | -1.6649e-06 | -0.00090641 | 4.8023 | 0 | 4.8014 |  | 15.2014 | 4 | 15.2014 | 70.0088 | 35.0044 | 15 | 35 | 0.0044051 | 0.2087 | 6.5155e-05 | 1.0405e-06 | 1 | 0
1130 | 18.8333 | 5 | 12.0001 | 5 | 12 | 70.0081 | 40 | -6.6707e-05 | 3.5495 | -1.552e-06 | -0.000928 | 4.8022 | 0 | 4.8013 |  | 15.2013 | 4 | 15.2013 | 70.0081 | 35.0041 | 15 | 35 | 0.0040556 | 0.21275 | 6.6707e-05 | 9.6999e-07 | 1 | 0
1131 | 18.85 | 5 | 12.0001 | 5 | 12 | 70.0074 | 40 | -6.8145e-05 | 3.5494 | -1.4384e-06 | -0.00094801 | 4.8021 | 0 | 4.8012 |  | 15.2012 | 4 | 15.2012 | 70.0074 | 35.0037 | 15 | 35 | 0.0037049 | 0.21646 | 6.8145e-05 | 8.99e-07 | 1 | 0
1132 | 18.8667 | 5 | 12.0001 | 5 | 12 | 70.0067 | 40 | -6.947e-05 | 3.5493 | -1.3243e-06 | -0.00096643 | 4.802 | 0 | 4.8011 |  | 15.2011 | 4 | 15.2011 | 70.0067 | 35.0034 | 15 | 35 | 0.0033536 | 0.21981 | 6.947e-05 | 8.2767e-07 | 1 | 0
1133 | 18.8833 | 5 | 12.0001 | 5 | 12 | 70.006 | 40 | -7.068e-05 | 3.5493 | -1.2098e-06 | -0.00098326 | 4.8019 | 0 | 4.801 |  | 15.201 | 4 | 15.201 | 70.006 | 35.003 | 15 | 35 | 0.0030022 | 0.22281 | 7.068e-05 | 7.5611e-07 | 1 | 0
1134 | 18.9 | 5 | 12.0001 | 5 | 12 | 70.0053 | 40 | -7.1775e-05 | 3.5492 | -1.0951e-06 | -0.0009985 | 4.8018 | 0 | 4.8008 |  | 15.2008 | 4 | 15.2008 | 70.0053 | 35.0027 | 15 | 35 | 0.0026512 | 0.22546 | 7.1775e-05 | 6.8442e-07 | 1 | 0
1135 | 18.9167 | 5 | 12.0001 | 5 | 12 | 70.0046 | 40 | -7.2755e-05 | 3.5491 | -9.8032e-07 | -0.0010121 | 4.8017 | 0 | 4.8007 |  | 15.2007 | 4 | 15.2007 | 70.0046 | 35.0023 | 15 | 35 | 0.0023009 | 0.22776 | 7.2755e-05 | 6.127e-07 | 1 | 0
1136 | 18.9333 | 5 | 12.0001 | 5 | 12 | 70.0039 | 40 | -7.3621e-05 | 3.549 | -8.6568e-07 | -0.0010242 | 4.8016 | 0 | 4.8006 |  | 15.2006 | 4 | 15.2006 | 70.0039 | 35.002 | 15 | 35 | 0.001952 | 0.22972 | 7.3621e-05 | 5.4105e-07 | 1 | 0
1137 | 18.95 | 5 | 12.0001 | 5 | 12 | 70.0032 | 40 | -7.4372e-05 | 3.549 | -7.5133e-07 | -0.0010346 | 4.8015 | 0 | 4.8005 |  | 15.2005 | 4 | 15.2005 | 70.0032 | 35.0016 | 15 | 35 | 0.0016049 | 0.23132 | 7.4372e-05 | 4.6958e-07 | 1 | 0
1138 | 18.9667 | 5 | 12.0001 | 5 | 12 | 70.0025 | 40 | -7.5009e-05 | 3.5489 | -6.374e-07 | -0.0010435 | 4.8014 | 0 | 4.8004 |  | 15.2004 | 4 | 15.2004 | 70.0025 | 35.0013 | 15 | 35 | 0.0012601 | 0.23258 | 7.5009e-05 | 3.9838e-07 | 1 | 0
1139 | 18.9833 | 5 | 12.0001 | 5 | 12 | 70.0018 | 40 | -7.5533e-05 | 3.5488 | -5.2406e-07 | -0.0010508 | 4.8013 | 0 | 4.8003 |  | 15.2003 | 4 | 15.2003 | 70.0018 | 35.0009 | 15 | 35 | 0.00091796 | 0.2335 | 7.5533e-05 | 3.2754e-07 | 1 | 0
1140 | 19 | 5 | 12.0001 | 5 | 12 | 70.0012 | 40 | -7.5945e-05 | 3.5487 | -4.1146e-07 | -0.0010565 | 4.8012 | 0 | 4.8002 |  | 15.2002 | 4 | 15.2002 | 70.0012 | 35.0006 | 15 | 35 | 0.00057898 | 0.23408 | 7.5945e-05 | 2.5716e-07 | 1 | 0
1141 | 19.0167 | 5 | 12.0001 | 5 | 12 | 70.0005 | 40 | -7.6245e-05 | 3.5487 | -2.9974e-07 | -0.0010607 | 4.8011 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0005 | 35.0002 | 15 | 35 | 0.00024359 | 0.23432 | 7.6245e-05 | 1.8734e-07 | 1 | 0
1142 | 19.0333 | 5 | 12.0001 | 5 | 12 | 69.9998 | 40 | -7.6434e-05 | 3.5486 | -1.8905e-07 | -0.0010633 | 4.801 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9998 | 34.9999 | 15 | 35 | -8.7785e-05 | 0.23423 | 7.6434e-05 | 1.1816e-07 | 1 | 0
1143 | 19.05 | 5 | 12.0001 | 5 | 12 | 69.9992 | 40 | -7.6513e-05 | 3.5485 | -7.954e-08 | -0.0010644 | 4.8009 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9992 | 34.9996 | 15 | 35 | -0.00041474 | 0.23382 | 7.6513e-05 | 4.9712e-08 | 1 | 0
1144 | 19.0667 | 5 | 12.0001 | 5 | 12 | 69.9985 | 40 | -7.6485e-05 | 3.5484 | 2.8665e-08 | -0.001064 | 4.8008 | 0 | 4.7998 |  | 15.1998 | 4 | 15.1998 | 69.9985 | 34.9993 | 15 | 35 | -0.00073686 | 0.23308 | 7.6485e-05 | -1.7915e-08 | -1 | -2
1145 | 19.0833 | 5 | 12.0001 | 5 | 12 | 69.9979 | 40 | -7.6349e-05 | 3.5484 | 1.3542e-07 | -0.0010621 | 4.8007 | 0 | 4.7997 |  | 15.1997 | 4 | 15.1997 | 69.9979 | 34.9989 | 15 | 35 | -0.0010538 | 0.23203 | 7.6349e-05 | -8.464e-08 | -1 | 0
1146 | 19.1 | 5 | 12.0001 | 5 | 12 | 69.9973 | 40 | -7.6108e-05 | 3.5483 | 2.4061e-07 | -0.0010588 | 4.8006 | 0 | 4.7996 |  | 15.1996 | 4 | 15.1996 | 69.9973 | 34.9986 | 15 | 35 | -0.0013651 | 0.23066 | 7.6108e-05 | -1.5038e-07 | -1 | 0
1147 | 19.1167 | 5 | 12.0001 | 5 | 12 | 69.9967 | 40 | -7.5764e-05 | 3.5482 | 3.4409e-07 | -0.001054 | 4.8005 | 0 | 4.7995 |  | 15.1995 | 4 | 15.1995 | 69.9967 | 34.9983 | 15 | 35 | -0.0016705 | 0.22899 | 7.5764e-05 | -2.1506e-07 | -1 | 0
1148 | 19.1333 | 5 | 12.0001 | 5 | 12 | 69.9961 | 40 | -7.5319e-05 | 3.5481 | 4.4575e-07 | -0.0010478 | 4.8004 | 0 | 4.7994 |  | 15.1994 | 4 | 15.1994 | 69.9961 | 34.998 | 15 | 35 | -0.0019695 | 0.22702 | 7.5319e-05 | -2.7859e-07 | -1 | 0
1149 | 19.15 | 5 | 12.0001 | 5 | 12 | 69.9955 | 40 | -7.4773e-05 | 3.5481 | 5.4546e-07 | -0.0010402 | 4.8003 | 0 | 4.7993 |  | 15.1993 | 4 | 15.1993 | 69.9955 | 34.9977 | 15 | 35 | -0.002262 | 0.22476 | 7.4773e-05 | -3.4091e-07 | -1 | 0
1150 | 19.1667 | 5 | 12.0001 | 5 | 12 | 69.9949 | 40 | -7.413e-05 | 3.548 | 6.4311e-07 | -0.0010313 | 4.8002 | 0 | 4.7992 |  | 15.1992 | 4 | 15.1992 | 69.9949 | 34.9975 | 15 | 35 | -0.0025474 | 0.22221 | 7.413e-05 | -4.0194e-07 | -1 | 0
1151 | 19.1833 | 5 | 12.0001 | 5 | 12 | 69.9943 | 40 | -7.3391e-05 | 3.5479 | 7.386e-07 | -0.001021 | 4.8001 | 0 | 4.7991 |  | 15.1991 | 4 | 15.1991 | 69.9943 | 34.9972 | 15 | 35 | -0.0028256 | 0.21939 | 7.3391e-05 | -4.6162e-07 | -1 | 0
1152 | 19.2 | 5 | 12.0001 | 5 | 12 | 69.9938 | 40 | -7.256e-05 | 3.5478 | 8.3181e-07 | -0.0010094 | 4.8 | 0 | 4.799 |  | 15.199 | 4 | 15.199 | 69.9938 | 34.9969 | 15 | 35 | -0.0030962 | 0.21629 | 7.256e-05 | -5.1988e-07 | -1 | 0
1153 | 19.2167 | 5 | 12.0001 | 5 | 12 | 69.9933 | 40 | -7.1637e-05 | 3.5478 | 9.2264e-07 | -0.00099658 | 4.7999 | 0 | 4.7989 |  | 15.1989 | 4 | 15.1989 | 69.9933 | 34.9966 | 15 | 35 | -0.003359 | 0.21293 | 7.1637e-05 | -5.7665e-07 | -1 | 0
1154 | 19.2333 | 5 | 12.0001 | 5 | 12 | 69.9928 | 40 | -7.0626e-05 | 3.5477 | 1.011e-06 | -0.00098252 | 4.7998 | 0 | 4.7988 |  | 15.1988 | 4 | 15.1988 | 69.9928 | 34.9964 | 15 | 35 | -0.0036136 | 0.20932 | 7.0626e-05 | -6.3188e-07 | -1 | 0
1155 | 19.25 | 5 | 12.0001 | 5 | 12 | 69.9923 | 40 | -6.9529e-05 | 3.5476 | 1.0968e-06 | -0.00096726 | 4.7997 | 0 | 4.7988 |  | 15.1988 | 4 | 15.1988 | 69.9923 | 34.9961 | 15 | 35 | -0.0038599 | 0.20546 | 6.9529e-05 | -6.8551e-07 | -1 | 0
1156 | 19.2667 | 5 | 12.0001 | 5 | 12 | 69.9918 | 40 | -6.8349e-05 | 3.5476 | 1.18e-06 | -0.00095084 | 4.7996 | 0 | 4.7987 |  | 15.1987 | 4 | 15.1987 | 69.9918 | 34.9959 | 15 | 35 | -0.0040976 | 0.20136 | 6.8349e-05 | -7.3748e-07 | -1 | 0
1157 | 19.2833 | 5 | 12.0001 | 5 | 12 | 69.9913 | 40 | -6.7089e-05 | 3.5475 | 1.2604e-06 | -0.00093331 | 4.7995 | 0 | 4.7986 |  | 15.1986 | 4 | 15.1986 | 69.9913 | 34.9957 | 15 | 35 | -0.0043264 | 0.19704 | 6.7089e-05 | -7.8774e-07 | -1 | 0
1158 | 19.3 | 5 | 12.0001 | 5 | 12 | 69.9909 | 40 | -6.5751e-05 | 3.5474 | 1.338e-06 | -0.0009147 | 4.7995 | 0 | 4.7985 |  | 15.1985 | 4 | 15.1985 | 69.9909 | 34.9955 | 15 | 35 | -0.0045463 | 0.19249 | 6.5751e-05 | -8.3624e-07 | -1 | 0
1159 | 19.3167 | 5 | 12.0001 | 5 | 12 | 69.9905 | 40 | -6.4338e-05 | 3.5474 | 1.4127e-06 | -0.00089504 | 4.7994 | 0 | 4.7985 |  | 15.1985 | 4 | 15.1985 | 69.9905 | 34.9952 | 15 | 35 | -0.0047569 | 0.18773 | 6.4338e-05 | -8.8295e-07 | -1 | 0
1160 | 19.3333 | 5 | 12.0001 | 5 | 12 | 69.9901 | 40 | -6.2854e-05 | 3.5473 | 1.4845e-06 | -0.00087439 | 4.7993 | 0 | 4.7984 |  | 15.1984 | 4 | 15.1984 | 69.9901 | 34.995 | 15 | 35 | -0.0049581 | 0.18277 | 6.2854e-05 | -9.2781e-07 | -1 | 0
1161 | 19.35 | 5 | 12.0001 | 5 | 12 | 69.9897 | 40 | -6.13e-05 | 3.5472 | 1.5533e-06 | -0.00085278 | 4.7992 | 0 | 4.7984 |  | 15.1984 | 4 | 15.1984 | 69.9897 | 34.9949 | 15 | 35 | -0.0051497 | 0.17762 | 6.13e-05 | -9.7079e-07 | -1 | 0
1162 | 19.3667 | 5 | 12.0001 | 5 | 12 | 69.9893 | 40 | -5.9681e-05 | 3.5472 | 1.619e-06 | -0.00083026 | 4.7991 | 0 | 4.7983 |  | 15.1983 | 4 | 15.1983 | 69.9893 | 34.9947 | 15 | 35 | -0.0053317 | 0.17229 | 5.9681e-05 | -1.0119e-06 | -1 | 0
1163 | 19.3833 | 5 | 12.0001 | 5 | 12 | 69.989 | 40 | -5.8e-05 | 3.5471 | 1.6815e-06 | -0.00080687 | 4.799 | 0 | 4.7982 |  | 15.1982 | 4 | 15.1982 | 69.989 | 34.9945 | 15 | 35 | -0.0055038 | 0.16679 | 5.8e-05 | -1.051e-06 | -1 | 0
1164 | 19.4 | 5 | 12.0001 | 5 | 12 | 69.9887 | 40 | -5.6259e-05 | 3.5471 | 1.741e-06 | -0.00078265 | 4.799 | 0 | 4.7982 |  | 15.1982 | 4 | 15.1982 | 69.9887 | 34.9943 | 15 | 35 | -0.005666 | 0.16112 | 5.6259e-05 | -1.0881e-06 | -1 | 0
1165 | 19.4167 | 5 | 12.0001 | 5 | 12 | 69.9884 | 40 | -5.4462e-05 | 3.547 | 1.7972e-06 | -0.00075765 | 4.7989 | 0 | 4.7981 |  | 15.1981 | 4 | 15.1981 | 69.9884 | 34.9942 | 15 | 35 | -0.0058181 | 0.15531 | 5.4462e-05 | -1.1232e-06 | -1 | 0
1166 | 19.4333 | 5 | 12.0001 | 5 | 12 | 69.9881 | 40 | -5.2612e-05 | 3.547 | 1.8501e-06 | -0.00073191 | 4.7988 | 0 | 4.7981 |  | 15.1981 | 4 | 15.1981 | 69.9881 | 34.994 | 15 | 35 | -0.0059601 | 0.14935 | 5.2612e-05 | -1.1563e-06 | -1 | 0
1167 | 19.45 | 5 | 12.0001 | 5 | 12 | 69.9878 | 40 | -5.0712e-05 | 3.5469 | 1.8998e-06 | -0.00070548 | 4.7988 | 0 | 4.7981 |  | 15.1981 | 4 | 15.1981 | 69.9878 | 34.9939 | 15 | 35 | -0.0060919 | 0.14325 | 5.0712e-05 | -1.1874e-06 | -1 | 0
1168 | 19.4667 | 5 | 12 | 5 | 12 | 69.9876 | 40 | -4.8766e-05 | 3.5469 | 1.9462e-06 | -0.00067841 | 4.7987 | 0 | 4.798 |  | 15.198 | 4 | 15.198 | 69.9876 | 34.9938 | 15 | 35 | -0.0062135 | 0.13704 | 4.8766e-05 | -1.2163e-06 | -1 | 0
1169 | 19.4833 | 5 | 12 | 5 | 12 | 69.9874 | 40 | -4.6777e-05 | 3.5468 | 1.9892e-06 | -0.00065073 | 4.7986 | 0 | 4.798 |  | 15.198 | 4 | 15.198 | 69.9874 | 34.9937 | 15 | 35 | -0.0063248 | 0.13071 | 4.6777e-05 | -1.2432e-06 | -1 | 0
1170 | 19.5 | 5 | 12 | 5 | 12 | 69.9871 | 40 | -4.4748e-05 | 3.5468 | 2.0289e-06 | -0.00062251 | 4.7986 | 0 | 4.7979 |  | 15.1979 | 4 | 15.1979 | 69.9871 | 34.9936 | 15 | 35 | -0.0064258 | 0.12429 | 4.4748e-05 | -1.2681e-06 | -1 | 0
1171 | 19.5167 | 5 | 12 | 5 | 12 | 69.987 | 40 | -4.2682e-05 | 3.5467 | 2.0652e-06 | -0.00059378 | 4.7985 | 0 | 4.7979 |  | 15.1979 | 4 | 15.1979 | 69.987 | 34.9935 | 15 | 35 | -0.0065164 | 0.11777 | 4.2682e-05 | -1.2908e-06 | -1 | 0
1172 | 19.5333 | 5 | 12 | 5 | 12 | 69.9868 | 40 | -4.0584e-05 | 3.5467 | 2.0982e-06 | -0.00056459 | 4.7985 | 0 | 4.7979 |  | 15.1979 | 4 | 15.1979 | 69.9868 | 34.9934 | 15 | 35 | -0.0065968 | 0.11118 | 4.0584e-05 | -1.3114e-06 | -1 | 0
1173 | 19.55 | 5 | 12 | 5 | 12 | 69.9867 | 40 | -3.8456e-05 | 3.5466 | 2.1278e-06 | -0.00053499 | 4.7984 | 0 | 4.7979 |  | 15.1979 | 4 | 15.1979 | 69.9867 | 34.9933 | 15 | 35 | -0.0066669 | 0.10451 | 3.8456e-05 | -1.3299e-06 | -1 | 0
1174 | 19.5667 | 5 | 12 | 5 | 12 | 69.9865 | 40 | -3.6302e-05 | 3.5466 | 2.1541e-06 | -0.00050502 | 4.7984 | 0 | 4.7978 |  | 15.1978 | 4 | 15.1978 | 69.9865 | 34.9933 | 15 | 35 | -0.0067267 | 0.097782 | 3.6302e-05 | -1.3463e-06 | -1 | 0
1175 | 19.5833 | 5 | 12 | 5 | 12 | 69.9864 | 40 | -3.4125e-05 | 3.5466 | 2.1769e-06 | -0.00047474 | 4.7983 | 0 | 4.7978 |  | 15.1978 | 4 | 15.1978 | 69.9864 | 34.9932 | 15 | 35 | -0.0067764 | 0.091006 | 3.4125e-05 | -1.3606e-06 | -1 | 0
1176 | 19.6 | 5 | 12 | 5 | 12 | 69.9864 | 40 | -3.1929e-05 | 3.5465 | 2.1965e-06 | -0.00044418 | 4.7983 | 0 | 4.7978 |  | 15.1978 | 4 | 15.1978 | 69.9864 | 34.9932 | 15 | 35 | -0.0068159 | 0.08419 | 3.1929e-05 | -1.3728e-06 | -1 | 0
1177 | 19.6167 | 5 | 12 | 5 | 12 | 69.9863 | 40 | -2.9716e-05 | 3.5465 | 2.2127e-06 | -0.0004134 | 4.7982 | 0 | 4.7978 |  | 15.1978 | 4 | 15.1978 | 69.9863 | 34.9932 | 15 | 35 | -0.0068453 | 0.077345 | 2.9716e-05 | -1.3829e-06 | -1 | 0
1178 | 19.6333 | 5 | 12 | 5 | 12 | 69.9863 | 40 | -2.7491e-05 | 3.5465 | 2.2256e-06 | -0.00038244 | 4.7982 | 0 | 4.7978 |  | 15.1978 | 4 | 15.1978 | 69.9863 | 34.9931 | 15 | 35 | -0.0068648 | 0.07048 | 2.7491e-05 | -1.391e-06 | -1 | 0
1179 | 19.65 | 5 | 12 | 5 | 12 | 69.9863 | 40 | -2.5255e-05 | 3.5465 | 2.2352e-06 | -0.00035134 | 4.7982 | 0 | 4.7978 |  | 15.1978 | 4 | 15.1978 | 69.9863 | 34.9931 | 15 | 35 | -0.0068744 | 0.063605 | 2.5255e-05 | -1.397e-06 | -1 | 0
1180 | 19.6667 | 5 | 12 | 5 | 12 | 69.9863 | 40 | -2.3014e-05 | 3.5464 | 2.2416e-06 | -0.00032016 | 4.7981 | 0 | 4.7978 |  | 15.1978 | 4 | 15.1978 | 69.9863 | 34.9931 | 15 | 35 | -0.0068743 | 0.056731 | 2.3014e-05 | -1.401e-06 | -1 | 0
1181 | 19.6833 | 5 | 12 | 5 | 12 | 69.9863 | 40 | -2.0769e-05 | 3.5464 | 2.2447e-06 | -0.00028893 | 4.7981 | 0 | 4.7978 |  | 15.1978 | 4 | 15.1978 | 69.9863 | 34.9931 | 15 | 35 | -0.0068645 | 0.049867 | 2.0769e-05 | -1.4029e-06 | -1 | 0
1182 | 19.7 | 5 | 12 | 5 | 12 | 69.9863 | 40 | -1.8524e-05 | 3.5464 | 2.2447e-06 | -0.0002577 | 4.7981 | 0 | 4.7978 |  | 15.1978 | 4 | 15.1978 | 69.9863 | 34.9932 | 15 | 35 | -0.0068452 | 0.043021 | 1.8524e-05 | -1.4029e-06 | -1 | 0
1183 | 19.7167 | 5 | 12 | 5 | 12 | 69.9864 | 40 | -1.6283e-05 | 3.5464 | 2.2415e-06 | -0.00022652 | 4.798 | 0 | 4.7978 |  | 15.1978 | 4 | 15.1978 | 69.9864 | 34.9932 | 15 | 35 | -0.0068166 | 0.036205 | 1.6283e-05 | -1.4009e-06 | -1 | 0
1184 | 19.7333 | 5 | 12 | 5 | 12 | 69.9864 | 40 | -1.4048e-05 | 3.5464 | 2.2352e-06 | -0.00019543 | 4.798 | 0 | 4.7978 |  | 15.1978 | 4 | 15.1978 | 69.9864 | 34.9932 | 15 | 35 | -0.0067788 | 0.029426 | 1.4048e-05 | -1.397e-06 | -1 | 0
1185 | 19.75 | 5 | 12 | 5 | 12 | 69.9865 | 40 | -1.1822e-05 | 3.5464 | 2.2258e-06 | -0.00016446 | 4.798 | 0 | 4.7978 |  | 15.1978 | 4 | 15.1978 | 69.9865 | 34.9933 | 15 | 35 | -0.0067321 | 0.022694 | 1.1822e-05 | -1.3911e-06 | -1 | 0
1186 | 19.7667 | 5 | 12 | 5 | 12 | 69.9866 | 40 | -9.6084e-06 | 3.5463 | 2.2135e-06 | -0.00013367 | 4.798 | 0 | 4.7979 |  | 15.1979 | 4 | 15.1979 | 69.9866 | 34.9933 | 15 | 35 | -0.0066765 | 0.016017 | 9.6084e-06 | -1.3834e-06 | -1 | 0
1187 | 19.7833 | 5 | 12 | 5 | 12 | 69.9868 | 40 | -7.4102e-06 | 3.5463 | 2.1982e-06 | -0.00010309 | 4.798 | 0 | 4.7979 |  | 15.1979 | 4 | 15.1979 | 69.9868 | 34.9934 | 15 | 35 | -0.0066122 | 0.0094051 | 7.4102e-06 | -1.3739e-06 | -1 | 0
1188 | 19.8 | 5 | 12 | 5 | 12 | 69.9869 | 40 | -5.2302e-06 | 3.5463 | 2.1801e-06 | -7.276e-05 | 4.798 | 0 | 4.7979 |  | 15.1979 | 4 | 15.1979 | 69.9869 | 34.9935 | 15 | 35 | -0.0065396 | 0.0028656 | 5.2302e-06 | -1.3625e-06 | -1 | 0
1189 | 19.8167 | 5 | 12 | 5 | 12 | 69.9871 | 40 | -3.0711e-06 | 3.5463 | 2.1591e-06 | -4.2723e-05 | 4.798 | 0 | 4.7979 |  | 15.1979 | 4 | 15.1979 | 69.9871 | 34.9935 | 15 | 35 | -0.0064587 | -0.0035931 | 3.0711e-06 | -1.3494e-06 | -1 | 0
1190 | 19.8333 | 5 | 12 | 5 | 12 | 69.9873 | 40 | -9.3569e-07 | 3.5463 | 2.1354e-06 | -1.3017e-05 | 4.798 | 0 | 4.798 |  | 15.198 | 4 | 15.198 | 69.9873 | 34.9936 | 15 | 35 | -0.0063698 | -0.0099629 | 9.3569e-07 | -1.3346e-06 | -1 | 0
1191 | 19.85 | 5 | 12 | 5 | 12 | 69.9875 | 40 | 1.1733e-06 | 3.5463 | 2.109e-06 | 1.6322e-05 | 4.798 | 0 | 4.798 |  | 15.198 | 4 | 15.198 | 69.9875 | 34.9937 | 15 | 35 | -0.0062732 | -0.016236 | 1.1733e-06 | -1.3181e-06 | -1 | 0
1192 | 19.8667 | 5 | 12 | 5 | 12 | 69.9877 | 40 | 3.2532e-06 | 3.5463 | 2.0799e-06 | 4.5257e-05 | 4.798 | 0 | 4.798 |  | 15.198 | 4 | 15.198 | 69.9877 | 34.9938 | 15 | 35 | -0.006169 | -0.022405 | 3.2532e-06 | -1.3e-06 | -1 | 0
1193 | 19.8833 | 5 | 12 | 5 | 12 | 69.9879 | 40 | 5.3016e-06 | 3.5463 | 2.0484e-06 | 7.3753e-05 | 4.798 | 0 | 4.7981 |  | 15.1981 | 4 | 15.1981 | 69.9879 | 34.9939 | 15 | 35 | -0.0060575 | -0.028463 | 5.3016e-06 | -1.2802e-06 | -1 | 0
1194 | 19.9 | 5 | 12 | 5 | 12 | 69.9881 | 40 | 7.3159e-06 | 3.5463 | 2.0144e-06 | 0.00010178 | 4.798 | 0 | 4.7981 |  | 15.1981 | 4 | 15.1981 | 69.9881 | 34.9941 | 15 | 35 | -0.005939 | -0.034402 | 7.3159e-06 | -1.259e-06 | -1 | 0
1195 | 19.9167 | 5 | 12 | 5 | 12 | 69.9884 | 40 | 9.2939e-06 | 3.5464 | 1.978e-06 | 0.00012929 | 4.798 | 0 | 4.7981 |  | 15.1981 | 4 | 15.1981 | 69.9884 | 34.9942 | 15 | 35 | -0.0058137 | -0.040215 | 9.2939e-06 | -1.2362e-06 | -1 | 0
1196 | 19.9333 | 5 | 12 | 5 | 12 | 69.9886 | 40 | 1.1233e-05 | 3.5464 | 1.9393e-06 | 0.00015627 | 4.798 | 0 | 4.7982 |  | 15.1982 | 4 | 15.1982 | 69.9886 | 34.9943 | 15 | 35 | -0.0056819 | -0.045897 | 1.1233e-05 | -1.212e-06 | -1 | 0
1197 | 19.95 | 5 | 12 | 5 | 12 | 69.9889 | 40 | 1.3132e-05 | 3.5464 | 1.8984e-06 | 0.00018268 | 4.798 | 0 | 4.7982 |  | 15.1982 | 4 | 15.1982 | 69.9889 | 34.9945 | 15 | 35 | -0.0055439 | -0.051441 | 1.3132e-05 | -1.1865e-06 | -1 | 0
1198 | 19.9667 | 5 | 12 | 5 | 12 | 69.9892 | 40 | 1.4987e-05 | 3.5464 | 1.8553e-06 | 0.00020849 | 4.7981 | 0 | 4.7983 |  | 15.1983 | 4 | 15.1983 | 69.9892 | 34.9946 | 15 | 35 | -0.0053999 | -0.056841 | 1.4987e-05 | -1.1596e-06 | -1 | 0
1199 | 19.9833 | 5 | 12 | 5 | 12 | 69.9895 | 40 | 1.6797e-05 | 3.5464 | 1.8102e-06 | 0.00023367 | 4.7981 | 0 | 4.7983 |  | 15.1983 | 4 | 15.1983 | 69.9895 | 34.9947 | 15 | 35 | -0.0052501 | -0.062091 | 1.6797e-05 | -1.1314e-06 | -1 | 0
1200 | 20 | 5 | 12 | 5 | 12 | 69.9898 | 40 | 1.856e-05 | 3.5464 | 1.7632e-06 | 0.0002582 | 4.7981 | 0 | 4.7984 |  | 15.1984 | 4 | 15.1984 | 69.9898 | 34.9949 | 15 | 35 | -0.005095 | -0.067186 | 1.856e-05 | -1.102e-06 | -1 | 0
1201 | 20.0167 | 5 | 12 | 5 | 12 | 69.9901 | 40 | 2.0275e-05 | 3.5465 | 1.7143e-06 | 0.00028205 | 4.7981 | 0 | 4.7984 |  | 15.1984 | 4 | 15.1984 | 69.9901 | 34.9951 | 15 | 35 | -0.0049348 | -0.072121 | 2.0275e-05 | -1.0715e-06 | -1 | 0
1202 | 20.0333 | 5 | 12 | 5 | 12 | 69.9905 | 40 | 2.1938e-05 | 3.5465 | 1.6637e-06 | 0.0003052 | 4.7982 | 0 | 4.7985 |  | 15.1985 | 4 | 15.1985 | 69.9905 | 34.9952 | 15 | 35 | -0.0047697 | -0.076891 | 2.1938e-05 | -1.0398e-06 | -1 | 0
1203 | 20.05 | 5 | 12 | 5 | 12 | 69.9908 | 40 | 2.355e-05 | 3.5465 | 1.6114e-06 | 0.00032761 | 4.7982 | 0 | 4.7985 |  | 15.1985 | 4 | 15.1985 | 69.9908 | 34.9954 | 15 | 35 | -0.0046001 | -0.081491 | 2.355e-05 | -1.0071e-06 | -1 | 0
1204 | 20.0667 | 5 | 12 | 5 | 12 | 69.9911 | 40 | 2.5107e-05 | 3.5465 | 1.5575e-06 | 0.00034928 | 4.7982 | 0 | 4.7986 |  | 15.1986 | 4 | 15.1986 | 69.9911 | 34.9956 | 15 | 35 | -0.0044262 | -0.085917 | 2.5107e-05 | -9.7341e-07 | -1 | 0
1205 | 20.0833 | 5 | 12 | 5 | 12 | 69.9915 | 40 | 2.6609e-05 | 3.5465 | 1.5021e-06 | 0.00037018 | 4.7983 | 0 | 4.7986 |  | 15.1986 | 4 | 15.1986 | 69.9915 | 34.9958 | 15 | 35 | -0.0042484 | -0.090165 | 2.6609e-05 | -9.3879e-07 | -1 | 0
1206 | 20.1 | 5 | 12 | 5 | 12 | 69.9919 | 40 | 2.8055e-05 | 3.5466 | 1.4453e-06 | 0.00039028 | 4.7983 | 0 | 4.7987 |  | 15.1987 | 4 | 15.1987 | 69.9919 | 34.9959 | 15 | 35 | -0.004067 | -0.094232 | 2.8055e-05 | -9.0331e-07 | -1 | 0
1207 | 20.1167 | 5 | 12 | 5 | 12 | 69.9922 | 40 | 2.9442e-05 | 3.5466 | 1.3872e-06 | 0.00040958 | 4.7983 | 0 | 4.7988 |  | 15.1988 | 4 | 15.1988 | 69.9922 | 34.9961 | 15 | 35 | -0.0038822 | -0.098115 | 2.9442e-05 | -8.6702e-07 | -1 | 0
1208 | 20.1333 | 5 | 12 | 5 | 12 | 69.9926 | 40 | 3.077e-05 | 3.5466 | 1.328e-06 | 0.00042806 | 4.7984 | 0 | 4.7988 |  | 15.1988 | 4 | 15.1988 | 69.9926 | 34.9963 | 15 | 35 | -0.0036944 | -0.10181 | 3.077e-05 | -8.2999e-07 | -1 | 0
1209 | 20.15 | 5 | 12 | 5 | 12 | 69.993 | 40 | 3.2037e-05 | 3.5467 | 1.2677e-06 | 0.00044569 | 4.7984 | 0 | 4.7989 |  | 15.1989 | 4 | 15.1989 | 69.993 | 34.9965 | 15 | 35 | -0.0035038 | -0.10531 | 3.2037e-05 | -7.9228e-07 | -1 | 0
1210 | 20.1667 | 5 | 12 | 5 | 12 | 69.9934 | 40 | 3.3244e-05 | 3.5467 | 1.2063e-06 | 0.00046247 | 4.7985 | 0 | 4.7989 |  | 15.1989 | 4 | 15.1989 | 69.9934 | 34.9967 | 15 | 35 | -0.0033108 | -0.10862 | 3.3244e-05 | -7.5395e-07 | -1 | 0
1211 | 20.1833 | 5 | 12 | 5 | 12 | 69.9938 | 40 | 3.4388e-05 | 3.5467 | 1.1441e-06 | 0.00047839 | 4.7985 | 0 | 4.799 |  | 15.199 | 4 | 15.199 | 69.9938 | 34.9969 | 15 | 35 | -0.0031157 | -0.11174 | 3.4388e-05 | -7.1506e-07 | -1 | 0
1212 | 20.2 | 5 | 12 | 5 | 12 | 69.9942 | 40 | 3.5469e-05 | 3.5468 | 1.0811e-06 | 0.00049343 | 4.7986 | 0 | 4.7991 |  | 15.1991 | 4 | 15.1991 | 69.9942 | 34.9971 | 15 | 35 | -0.0029187 | -0.11466 | 3.5469e-05 | -6.7567e-07 | -1 | 0
1213 | 20.2167 | 5 | 12 | 5 | 12 | 69.9946 | 40 | 3.6486e-05 | 3.5468 | 1.0174e-06 | 0.00050758 | 4.7986 | 0 | 4.7991 |  | 15.1991 | 4 | 15.1991 | 69.9946 | 34.9973 | 15 | 35 | -0.0027202 | -0.11738 | 3.6486e-05 | -6.3585e-07 | -1 | 0
1214 | 20.2333 | 5 | 12 | 5 | 12 | 69.995 | 40 | 3.7439e-05 | 3.5468 | 9.5305e-07 | 0.00052084 | 4.7987 | 0 | 4.7992 |  | 15.1992 | 4 | 15.1992 | 69.995 | 34.9975 | 15 | 35 | -0.0025205 | -0.1199 | 3.7439e-05 | -5.9566e-07 | -1 | 0
1215 | 20.25 | 5 | 12 | 5 | 12 | 69.9954 | 40 | 3.8328e-05 | 3.5469 | 8.8824e-07 | 0.0005332 | 4.7987 | 0 | 4.7993 |  | 15.1993 | 4 | 15.1993 | 69.9954 | 34.9977 | 15 | 35 | -0.0023198 | -0.12222 | 3.8328e-05 | -5.5515e-07 | -1 | 0
1216 | 20.2667 | 5 | 12 | 5 | 12 | 69.9958 | 40 | 3.9151e-05 | 3.5469 | 8.2302e-07 | 0.00054465 | 4.7988 | 0 | 4.7993 |  | 15.1993 | 4 | 15.1993 | 69.9958 | 34.9979 | 15 | 35 | -0.0021185 | -0.12434 | 3.9151e-05 | -5.1439e-07 | -1 | 0
1217 | 20.2833 | 5 | 12 | 5 | 12 | 69.9962 | 40 | 3.9908e-05 | 3.547 | 7.575e-07 | 0.00055518 | 4.7988 | 0 | 4.7994 |  | 15.1994 | 4 | 15.1994 | 69.9962 | 34.9981 | 15 | 35 | -0.0019169 | -0.12625 | 3.9908e-05 | -4.7344e-07 | -1 | 0
1218 | 20.3 | 5 | 12 | 5 | 12 | 69.9966 | 40 | 4.06e-05 | 3.547 | 6.9177e-07 | 0.00056481 | 4.7989 | 0 | 4.7995 |  | 15.1995 | 4 | 15.1995 | 69.9966 | 34.9983 | 15 | 35 | -0.0017151 | -0.12797 | 4.06e-05 | -4.3235e-07 | -1 | 0
1219 | 20.3167 | 5 | 12 | 5 | 12 | 69.997 | 40 | 4.1226e-05 | 3.547 | 6.2592e-07 | 0.00057351 | 4.7989 | 0 | 4.7995 |  | 15.1995 | 4 | 15.1995 | 69.997 | 34.9985 | 15 | 35 | -0.0015136 | -0.12948 | 4.1226e-05 | -3.912e-07 | -1 | 0
1220 | 20.3333 | 5 | 12 | 5 | 12 | 69.9974 | 40 | 4.1786e-05 | 3.5471 | 5.6005e-07 | 0.00058131 | 4.799 | 0 | 4.7996 |  | 15.1996 | 4 | 15.1996 | 69.9974 | 34.9987 | 15 | 35 | -0.0013126 | -0.1308 | 4.1786e-05 | -3.5003e-07 | -1 | 0
1221 | 20.35 | 5 | 12 | 5 | 12 | 69.9978 | 40 | 4.228e-05 | 3.5471 | 4.9425e-07 | 0.00058818 | 4.7991 | 0 | 4.7996 |  | 15.1996 | 4 | 15.1996 | 69.9978 | 34.9989 | 15 | 35 | -0.0011124 | -0.13191 | 4.228e-05 | -3.089e-07 | -1 | 0
1222 | 20.3667 | 5 | 12 | 5 | 12 | 69.9982 | 40 | 4.2709e-05 | 3.5472 | 4.2861e-07 | 0.00059414 | 4.7991 | 0 | 4.7997 |  | 15.1997 | 4 | 15.1997 | 69.9982 | 34.9991 | 15 | 35 | -0.00091317 | -0.13282 | 4.2709e-05 | -2.6788e-07 | -1 | 0
1223 | 20.3833 | 5 | 12 | 5 | 12 | 69.9986 | 40 | 4.3072e-05 | 3.5472 | 3.6322e-07 | 0.0005992 | 4.7992 | 0 | 4.7998 |  | 15.1998 | 4 | 15.1998 | 69.9986 | 34.9993 | 15 | 35 | -0.00071528 | -0.13354 | 4.3072e-05 | -2.2702e-07 | -1 | 0
1224 | 20.4 | 5 | 12 | 5 | 12 | 69.999 | 40 | 4.337e-05 | 3.5473 | 2.9818e-07 | 0.00060334 | 4.7992 | 0 | 4.7998 |  | 15.1998 | 4 | 15.1998 | 69.999 | 34.9995 | 15 | 35 | -0.00051895 | -0.13406 | 4.337e-05 | -1.8636e-07 | -1 | 0
1225 | 20.4167 | 5 | 12 | 5 | 12 | 69.9994 | 40 | 4.3604e-05 | 3.5473 | 2.3356e-07 | 0.00060659 | 4.7993 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9994 | 34.9997 | 15 | 35 | -0.00032444 | -0.13438 | 4.3604e-05 | -1.4597e-07 | -1 | 0
1226 | 20.4333 | 5 | 12 | 5 | 12 | 69.9997 | 40 | 4.3773e-05 | 3.5473 | 1.6945e-07 | 0.00060895 | 4.7993 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9997 | 34.9999 | 15 | 35 | -0.000132 | -0.13451 | 4.3773e-05 | -1.0591e-07 | -1 | 0
1227 | 20.45 | 5 | 12 | 5 | 12 | 70.0001 | 40 | 4.3879e-05 | 3.5474 | 1.0594e-07 | 0.00061043 | 4.7994 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35.0001 | 15 | 35 | 5.812e-05 | -0.13445 | 4.3879e-05 | -6.6212e-08 | -1 | 0
1228 | 20.4667 | 5 | 12 | 5 | 12 | 70.0005 | 40 | 4.3922e-05 | 3.5474 | 4.3103e-08 | 0.00061102 | 4.7995 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0005 | 35.0002 | 15 | 35 | 0.00024569 | -0.13421 | 4.3922e-05 | -2.6939e-08 | -1 | 0
1229 | 20.4833 | 5 | 12 | 5 | 12 | 70.0009 | 40 | 4.3903e-05 | 3.5475 | -1.8978e-08 | 0.00061076 | 4.7995 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0009 | 35.0004 | 15 | 35 | 0.00043049 | -0.13378 | 4.3903e-05 | 1.1861e-08 | 1 | 2
1230 | 20.5 | 5 | 12 | 5 | 12 | 70.0012 | 40 | 4.3823e-05 | 3.5475 | -8.0227e-08 | 0.00060964 | 4.7996 | 0 | 4.8002 |  | 15.2002 | 4 | 15.2002 | 70.0012 | 35.0006 | 15 | 35 | 0.00061228 | -0.13316 | 4.3823e-05 | 5.0142e-08 | 1 | 0
1231 | 20.5167 | 5 | 12 | 5 | 12 | 70.0016 | 40 | 4.3682e-05 | 3.5476 | -1.4057e-07 | 0.00060769 | 4.7996 | 0 | 4.8003 |  | 15.2003 | 4 | 15.2003 | 70.0016 | 35.0008 | 15 | 35 | 0.00079086 | -0.13237 | 4.3682e-05 | 8.7855e-08 | 1 | 0
1232 | 20.5333 | 5 | 12 | 5 | 12 | 70.0019 | 40 | 4.3482e-05 | 3.5476 | -1.9993e-07 | 0.00060491 | 4.7997 | 0 | 4.8003 |  | 15.2003 | 4 | 15.2003 | 70.0019 | 35.001 | 15 | 35 | 0.00096601 | -0.13141 | 4.3482e-05 | 1.2496e-07 | 1 | 0
1233 | 20.55 | 5 | 12 | 5 | 12 | 70.0023 | 40 | 4.3224e-05 | 3.5477 | -2.5824e-07 | 0.00060132 | 4.7998 | 0 | 4.8004 |  | 15.2004 | 4 | 15.2004 | 70.0023 | 35.0011 | 15 | 35 | 0.0011375 | -0.13027 | 4.3224e-05 | 1.614e-07 | 1 | 0
1234 | 20.5667 | 5 | 12 | 5 | 12 | 70.0026 | 40 | 4.2909e-05 | 3.5477 | -3.1543e-07 | 0.00059693 | 4.7998 | 0 | 4.8004 |  | 15.2004 | 4 | 15.2004 | 70.0026 | 35.0013 | 15 | 35 | 0.0013052 | -0.12897 | 4.2909e-05 | 1.9714e-07 | 1 | 0
1235 | 20.5833 | 5 | 12 | 5 | 12 | 70.0029 | 40 | 4.2537e-05 | 3.5477 | -3.7144e-07 | 0.00059176 | 4.7999 | 0 | 4.8005 |  | 15.2005 | 4 | 15.2005 | 70.0029 | 35.0015 | 15 | 35 | 0.0014689 | -0.1275 | 4.2537e-05 | 2.3215e-07 | 1 | 0
1236 | 20.6 | 5 | 12 | 5 | 12 | 70.0033 | 40 | 4.2111e-05 | 3.5478 | -4.262e-07 | 0.00058583 | 4.7999 | 0 | 4.8005 |  | 15.2005 | 4 | 15.2005 | 70.0033 | 35.0016 | 15 | 35 | 0.0016284 | -0.12587 | 4.2111e-05 | 2.6637e-07 | 1 | 0
1237 | 20.6167 | 5 | 12 | 5 | 12 | 70.0036 | 40 | 4.1631e-05 | 3.5478 | -4.7965e-07 | 0.00057916 | 4.8 | 0 | 4.8006 |  | 15.2006 | 4 | 15.2006 | 70.0036 | 35.0018 | 15 | 35 | 0.0017836 | -0.12408 | 4.1631e-05 | 2.9978e-07 | 1 | 0
1238 | 20.6333 | 5 | 12 | 5 | 12 | 70.0039 | 40 | 4.11e-05 | 3.5479 | -5.3174e-07 | 0.00057176 | 4.8 | 0 | 4.8006 |  | 15.2006 | 4 | 15.2006 | 70.0039 | 35.0019 | 15 | 35 | 0.0019343 | -0.12215 | 4.11e-05 | 3.3234e-07 | 1 | 0
1239 | 20.65 | 5 | 12 | 5 | 12 | 70.0042 | 40 | 4.0517e-05 | 3.5479 | -5.824e-07 | 0.00056366 | 4.8001 | 0 | 4.8007 |  | 15.2007 | 4 | 15.2007 | 70.0042 | 35.0021 | 15 | 35 | 0.0020802 | -0.12007 | 4.0517e-05 | 3.64e-07 | 1 | 0
1240 | 20.6667 | 5 | 12 | 5 | 12 | 70.0044 | 40 | 3.9886e-05 | 3.5479 | -6.3159e-07 | 0.00055487 | 4.8002 | 0 | 4.8007 |  | 15.2007 | 4 | 15.2007 | 70.0044 | 35.0022 | 15 | 35 | 0.0022214 | -0.11785 | 3.9886e-05 | 3.9475e-07 | 1 | 0
1241 | 20.6833 | 5 | 12 | 5 | 12 | 70.0047 | 40 | 3.9206e-05 | 3.548 | -6.7926e-07 | 0.00054542 | 4.8002 | 0 | 4.8008 |  | 15.2008 | 4 | 15.2008 | 70.0047 | 35.0024 | 15 | 35 | 0.0023577 | -0.11549 | 3.9206e-05 | 4.2454e-07 | 1 | 0
1242 | 20.7 | 5 | 12 | 5 | 12 | 70.005 | 40 | 3.8481e-05 | 3.548 | -7.2536e-07 | 0.00053533 | 4.8003 | 0 | 4.8008 |  | 15.2008 | 4 | 15.2008 | 70.005 | 35.0025 | 15 | 35 | 0.0024888 | -0.113 | 3.8481e-05 | 4.5335e-07 | 1 | 0
1243 | 20.7167 | 5 | 12 | 5 | 12 | 70.0052 | 40 | 3.7711e-05 | 3.5481 | -7.6985e-07 | 0.00052462 | 4.8003 | 0 | 4.8008 |  | 15.2008 | 4 | 15.2008 | 70.0052 | 35.0026 | 15 | 35 | 0.0026148 | -0.11039 | 3.7711e-05 | 4.8115e-07 | 1 | 0
1244 | 20.7333 | 5 | 12 | 5 | 12 | 70.0055 | 40 | 3.6899e-05 | 3.5481 | -8.1267e-07 | 0.00051332 | 4.8004 | 0 | 4.8009 |  | 15.2009 | 4 | 15.2009 | 70.0055 | 35.0027 | 15 | 35 | 0.0027355 | -0.10765 | 3.6899e-05 | 5.0792e-07 | 1 | 0
1245 | 20.75 | 5 | 12 | 5 | 12 | 70.0057 | 40 | 3.6045e-05 | 3.5481 | -8.5381e-07 | 0.00050144 | 4.8004 | 0 | 4.8009 |  | 15.2009 | 4 | 15.2009 | 70.0057 | 35.0029 | 15 | 35 | 0.0028507 | -0.1048 | 3.6045e-05 | 5.3363e-07 | 1 | 0
1246 | 20.7667 | 5 | 12 | 5 | 12 | 70.0059 | 40 | 3.5152e-05 | 3.5482 | -8.9321e-07 | 0.00048901 | 4.8005 | 0 | 4.8009 |  | 15.2009 | 4 | 15.2009 | 70.0059 | 35.003 | 15 | 35 | 0.0029605 | -0.10184 | 3.5152e-05 | 5.5826e-07 | 1 | 0
1247 | 20.7833 | 5 | 12 | 5 | 12 | 70.0061 | 40 | 3.4221e-05 | 3.5482 | -9.3085e-07 | 0.00047606 | 4.8005 | 0 | 4.801 |  | 15.201 | 4 | 15.201 | 70.0061 | 35.0031 | 15 | 35 | 0.0030647 | -0.098776 | 3.4221e-05 | 5.8178e-07 | 1 | 0
1248 | 20.8 | 5 | 12 | 5 | 12 | 70.0063 | 40 | 3.3254e-05 | 3.5482 | -9.667e-07 | 0.00046261 | 4.8005 | 0 | 4.801 |  | 15.201 | 4 | 15.201 | 70.0063 | 35.0032 | 15 | 35 | 0.0031633 | -0.095612 | 3.3254e-05 | 6.0419e-07 | 1 | 0
1249 | 20.8167 | 5 | 12 | 5 | 12 | 70.0065 | 40 | 3.2253e-05 | 3.5483 | -1.0007e-06 | 0.00044869 | 4.8006 | 0 | 4.801 |  | 15.201 | 4 | 15.201 | 70.0065 | 35.0033 | 15 | 35 | 0.0032562 | -0.092356 | 3.2253e-05 | 6.2546e-07 | 1 | 0
1250 | 20.8333 | 5 | 12 | 5 | 12 | 70.0067 | 40 | 3.122e-05 | 3.5483 | -1.0329e-06 | 0.00043432 | 4.8006 | 0 | 4.8011 |  | 15.2011 | 4 | 15.2011 | 70.0067 | 35.0033 | 15 | 35 | 0.0033433 | -0.089013 | 3.122e-05 | 6.4557e-07 | 1 | 0
1251 | 20.85 | 5 | 12 | 5 | 12 | 70.0068 | 40 | 3.0157e-05 | 3.5483 | -1.0632e-06 | 0.00041953 | 4.8007 | 0 | 4.8011 |  | 15.2011 | 4 | 15.2011 | 70.0068 | 35.0034 | 15 | 35 | 0.0034245 | -0.085588 | 3.0157e-05 | 6.6452e-07 | 1 | 0
1252 | 20.8667 | 5 | 12 | 5 | 12 | 70.007 | 40 | 2.9065e-05 | 3.5484 | -1.0917e-06 | 0.00040435 | 4.8007 | 0 | 4.8011 |  | 15.2011 | 4 | 15.2011 | 70.007 | 35.0035 | 15 | 35 | 0.0035 | -0.082088 | 2.9065e-05 | 6.823e-07 | 1 | 0
1253 | 20.8833 | 5 | 12 | 5 | 12 | 70.0071 | 40 | 2.7947e-05 | 3.5484 | -1.1182e-06 | 0.00038879 | 4.8008 | 0 | 4.8011 |  | 15.2011 | 4 | 15.2011 | 70.0071 | 35.0036 | 15 | 35 | 0.0035695 | -0.078519 | 2.7947e-05 | 6.9889e-07 | 1 | 0
1254 | 20.9 | 5 | 12 | 5 | 12 | 70.0073 | 40 | 2.6804e-05 | 3.5484 | -1.1428e-06 | 0.00037289 | 4.8008 | 0 | 4.8012 |  | 15.2012 | 4 | 15.2012 | 70.0073 | 35.0036 | 15 | 35 | 0.0036332 | -0.074886 | 2.6804e-05 | 7.1428e-07 | 1 | 0
1255 | 20.9167 | 5 | 12 | 5 | 12 | 70.0074 | 40 | 2.5639e-05 | 3.5484 | -1.1656e-06 | 0.00035668 | 4.8008 | 0 | 4.8012 |  | 15.2012 | 4 | 15.2012 | 70.0074 | 35.0037 | 15 | 35 | 0.0036909 | -0.071195 | 2.5639e-05 | 7.2847e-07 | 1 | 0
1256 | 20.9333 | 5 | 12 | 5 | 12 | 70.0075 | 40 | 2.4452e-05 | 3.5485 | -1.1863e-06 | 0.00034017 | 4.8009 | 0 | 4.8012 |  | 15.2012 | 4 | 15.2012 | 70.0075 | 35.0037 | 15 | 35 | 0.0037427 | -0.067452 | 2.4452e-05 | 7.4146e-07 | 1 | 0
1257 | 20.95 | 5 | 12 | 5 | 12 | 70.0076 | 40 | 2.3247e-05 | 3.5485 | -1.2052e-06 | 0.00032341 | 4.8009 | 0 | 4.8012 |  | 15.2012 | 4 | 15.2012 | 70.0076 | 35.0038 | 15 | 35 | 0.0037886 | -0.063663 | 2.3247e-05 | 7.5324e-07 | 1 | 0
1258 | 20.9667 | 5 | 12 | 5 | 12 | 70.0077 | 40 | 2.2025e-05 | 3.5485 | -1.2221e-06 | 0.0003064 | 4.8009 | 0 | 4.8012 |  | 15.2012 | 4 | 15.2012 | 70.0077 | 35.0038 | 15 | 35 | 0.0038286 | -0.059835 | 2.2025e-05 | 7.6382e-07 | 1 | 0
1259 | 20.9833 | 5 | 12 | 5 | 12 | 70.0077 | 40 | 2.0788e-05 | 3.5485 | -1.2371e-06 | 0.00028919 | 4.8009 | 0 | 4.8012 |  | 15.2012 | 4 | 15.2012 | 70.0077 | 35.0039 | 15 | 35 | 0.0038627 | -0.055972 | 2.0788e-05 | 7.7318e-07 | 1 | 0
1260 | 21 | 5 | 12 | 5 | 12 | 70.0078 | 40 | 1.9538e-05 | 3.5485 | -1.2502e-06 | 0.0002718 | 4.801 | 0 | 4.8012 |  | 15.2012 | 4 | 15.2012 | 70.0078 | 35.0039 | 15 | 35 | 0.003891 | -0.052081 | 1.9538e-05 | 7.8134e-07 | 1 | 0
1261 | 21.0167 | 5 | 12 | 5 | 12 | 70.0078 | 40 | 1.8277e-05 | 3.5486 | -1.2613e-06 | 0.00025426 | 4.801 | 0 | 4.8013 |  | 15.2013 | 4 | 15.2013 | 70.0078 | 35.0039 | 15 | 35 | 0.0039134 | -0.048168 | 1.8277e-05 | 7.8831e-07 | 1 | 0
1262 | 21.0333 | 5 | 12 | 5 | 12 | 70.0079 | 40 | 1.7006e-05 | 3.5486 | -1.2705e-06 | 0.00023658 | 4.801 | 0 | 4.8013 |  | 15.2013 | 4 | 15.2013 | 70.0079 | 35.0039 | 15 | 35 | 0.0039301 | -0.044238 | 1.7006e-05 | 7.9407e-07 | 1 | 0
1263 | 21.05 | 5 | 12 | 5 | 12 | 70.0079 | 40 | 1.5728e-05 | 3.5486 | -1.2778e-06 | 0.0002188 | 4.801 | 0 | 4.8013 |  | 15.2013 | 4 | 15.2013 | 70.0079 | 35.0039 | 15 | 35 | 0.003941 | -0.040297 | 1.5728e-05 | 7.9865e-07 | 1 | 0
1264 | 21.0667 | 5 | 12 | 5 | 12 | 70.0079 | 40 | 1.4445e-05 | 3.5486 | -1.2833e-06 | 0.00020095 | 4.8011 | 0 | 4.8013 |  | 15.2013 | 4 | 15.2013 | 70.0079 | 35.0039 | 15 | 35 | 0.0039463 | -0.036351 | 1.4445e-05 | 8.0205e-07 | 1 | 0
1265 | 21.0833 | 5 | 12 | 5 | 12 | 70.0079 | 40 | 1.3158e-05 | 3.5486 | -1.2869e-06 | 0.00018305 | 4.8011 | 0 | 4.8013 |  | 15.2013 | 4 | 15.2013 | 70.0079 | 35.0039 | 15 | 35 | 0.003946 | -0.032405 | 1.3158e-05 | 8.0429e-07 | 1 | 0
1266 | 21.1 | 5 | 12 | 5 | 12 | 70.0079 | 40 | 1.187e-05 | 3.5486 | -1.2886e-06 | 0.00016512 | 4.8011 | 0 | 4.8013 |  | 15.2013 | 4 | 15.2013 | 70.0079 | 35.0039 | 15 | 35 | 0.0039401 | -0.028464 | 1.187e-05 | 8.0536e-07 | 1 | 0
1267 | 21.1167 | 5 | 12 | 5 | 12 | 70.0079 | 40 | 1.0581e-05 | 3.5486 | -1.2885e-06 | 0.0001472 | 4.8011 | 0 | 4.8013 |  | 15.2013 | 4 | 15.2013 | 70.0079 | 35.0039 | 15 | 35 | 0.0039289 | -0.024536 | 1.0581e-05 | 8.053e-07 | 1 | 0
1268 | 21.1333 | 5 | 12 | 5 | 12 | 70.0078 | 40 | 9.2945e-06 | 3.5487 | -1.2866e-06 | 0.0001293 | 4.8011 | 0 | 4.8013 |  | 15.2013 | 4 | 15.2013 | 70.0078 | 35.0039 | 15 | 35 | 0.0039122 | -0.020623 | 9.2945e-06 | 8.0411e-07 | 1 | 0
1269 | 21.15 | 5 | 12 | 5 | 12 | 70.0078 | 40 | 8.0116e-06 | 3.5487 | -1.2829e-06 | 0.00011145 | 4.8011 | 0 | 4.8012 |  | 15.2012 | 4 | 15.2012 | 70.0078 | 35.0039 | 15 | 35 | 0.0038903 | -0.016733 | 8.0116e-06 | 8.0181e-07 | 1 | 0
1270 | 21.1667 | 5 | 12 | 5 | 12 | 70.0077 | 40 | 6.7341e-06 | 3.5487 | -1.2775e-06 | 9.3682e-05 | 4.8011 | 0 | 4.8012 |  | 15.2012 | 4 | 15.2012 | 70.0077 | 35.0039 | 15 | 35 | 0.0038633 | -0.01287 | 6.7341e-06 | 7.9841e-07 | 1 | 0
1271 | 21.1833 | 5 | 12 | 5 | 12 | 70.0077 | 40 | 5.4638e-06 | 3.5487 | -1.2703e-06 | 7.601e-05 | 4.8011 | 0 | 4.8012 |  | 15.2012 | 4 | 15.2012 | 70.0077 | 35.0038 | 15 | 35 | 0.0038311 | -0.0090386 | 5.4638e-06 | 7.9394e-07 | 1 | 0
1272 | 21.2 | 5 | 12 | 5 | 12 | 70.0076 | 40 | 4.2024e-06 | 3.5487 | -1.2615e-06 | 5.8461e-05 | 4.8012 | 0 | 4.8012 |  | 15.2012 | 4 | 15.2012 | 70.0076 | 35.0038 | 15 | 35 | 0.0037941 | -0.0052445 | 4.2024e-06 | 7.8842e-07 | 1 | 0
1273 | 21.2167 | 5 | 12 | 5 | 12 | 70.0075 | 40 | 2.9514e-06 | 3.5487 | -1.251e-06 | 4.1058e-05 | 4.8012 | 0 | 4.8012 |  | 15.2012 | 4 | 15.2012 | 70.0075 | 35.0038 | 15 | 35 | 0.0037522 | -0.0014924 | 2.9514e-06 | 7.8186e-07 | 1 | 0
1274 | 21.2333 | 5 | 12 | 5 | 12 | 70.0074 | 40 | 1.7125e-06 | 3.5487 | -1.2389e-06 | 2.3823e-05 | 4.8012 | 0 | 4.8012 |  | 15.2012 | 4 | 15.2012 | 70.0074 | 35.0037 | 15 | 35 | 0.0037055 | 0.0022132 | 1.7125e-06 | 7.743e-07 | 1 | 0
1275 | 21.25 | 5 | 12 | 5 | 12 | 70.0073 | 40 | 4.873e-07 | 3.5487 | -1.2252e-06 | 6.7791e-06 | 4.8012 | 0 | 4.8012 |  | 15.2012 | 4 | 15.2012 | 70.0073 | 35.0037 | 15 | 35 | 0.0036543 | 0.0058675 | 4.873e-07 | 7.6575e-07 | 1 | 0
1276 | 21.2667 | 5 | 12 | 5 | 12 | 70.0072 | 40 | -7.2267e-07 | 3.5487 | -1.21e-06 | -1.0054e-05 | 4.8012 | 0 | 4.8012 |  | 15.2012 | 4 | 15.2012 | 70.0072 | 35.0036 | 15 | 35 | 0.0035987 | 0.0094662 | 7.2267e-07 | 7.5623e-07 | 1 | 0
1277 | 21.2833 | 5 | 12 | 5 | 12 | 70.0071 | 40 | -1.9159e-06 | 3.5487 | -1.1933e-06 | -2.6654e-05 | 4.8012 | 0 | 4.8011 |  | 15.2011 | 4 | 15.2011 | 70.0071 | 35.0035 | 15 | 35 | 0.0035387 | 0.013005 | 1.9159e-06 | 7.4578e-07 | 1 | 0
1278 | 21.3 | 5 | 12 | 5 | 12 | 70.0069 | 40 | -3.091e-06 | 3.5487 | -1.1751e-06 | -4.3001e-05 | 4.8012 | 0 | 4.8011 |  | 15.2011 | 4 | 15.2011 | 70.0069 | 35.0035 | 15 | 35 | 0.0034745 | 0.016479 | 3.091e-06 | 7.3442e-07 | 1 | 0
1279 | 21.3167 | 5 | 12 | 5 | 12 | 70.0068 | 40 | -4.2465e-06 | 3.5487 | -1.1555e-06 | -5.9075e-05 | 4.8011 | 0 | 4.8011 |  | 15.2011 | 4 | 15.2011 | 70.0068 | 35.0034 | 15 | 35 | 0.0034064 | 0.019886 | 4.2465e-06 | 7.2218e-07 | 1 | 0
1280 | 21.3333 | 5 | 12 | 5 | 12 | 70.0067 | 40 | -5.381e-06 | 3.5487 | -1.1345e-06 | -7.4859e-05 | 4.8011 | 0 | 4.8011 |  | 15.2011 | 4 | 15.2011 | 70.0067 | 35.0033 | 15 | 35 | 0.0033343 | 0.02322 | 5.381e-06 | 7.0909e-07 | 1 | 0
1281 | 21.35 | 5 | 12 | 5 | 12 | 70.0065 | 40 | -6.4933e-06 | 3.5487 | -1.1123e-06 | -9.0332e-05 | 4.8011 | 0 | 4.801 |  | 15.201 | 4 | 15.201 | 70.0065 | 35.0033 | 15 | 35 | 0.0032585 | 0.026479 | 6.4933e-06 | 6.9518e-07 | 1 | 0
1282 | 21.3667 | 5 | 12 | 5 | 12 | 70.0064 | 40 | -7.5821e-06 | 3.5487 | -1.0887e-06 | -0.00010548 | 4.8011 | 0 | 4.801 |  | 15.201 | 4 | 15.201 | 70.0064 | 35.0032 | 15 | 35 | 0.0031791 | 0.029658 | 7.5821e-06 | 6.8047e-07 | 1 | 0
1283 | 21.3833 | 5 | 12 | 5 | 12 | 70.0062 | 40 | -8.6461e-06 | 3.5486 | -1.064e-06 | -0.00012028 | 4.8011 | 0 | 4.801 |  | 15.201 | 4 | 15.201 | 70.0062 | 35.0031 | 15 | 35 | 0.0030963 | 0.032754 | 8.6461e-06 | 6.65e-07 | 1 | 0
1284 | 21.4 | 5 | 12 | 5 | 12 | 70.006 | 40 | -9.6841e-06 | 3.5486 | -1.0381e-06 | -0.00013472 | 4.8011 | 0 | 4.801 |  | 15.201 | 4 | 15.201 | 70.006 | 35.003 | 15 | 35 | 0.0030102 | 0.035764 | 9.6841e-06 | 6.4879e-07 | 1 | 0
1285 | 21.4167 | 5 | 12 | 5 | 12 | 70.0058 | 40 | -1.0695e-05 | 3.5486 | -1.011e-06 | -0.00014879 | 4.8011 | 0 | 4.8009 |  | 15.2009 | 4 | 15.2009 | 70.0058 | 35.0029 | 15 | 35 | 0.002921 | 0.038685 | 1.0695e-05 | 6.3189e-07 | 1 | 0
1286 | 21.4333 | 5 | 12 | 5 | 12 | 70.0057 | 40 | -1.1678e-05 | 3.5486 | -9.8293e-07 | -0.00016246 | 4.8011 | 0 | 4.8009 |  | 15.2009 | 4 | 15.2009 | 70.0057 | 35.0028 | 15 | 35 | 0.0028289 | 0.041514 | 1.1678e-05 | 6.1433e-07 | 1 | 0
1287 | 21.45 | 5 | 12 | 5 | 12 | 70.0055 | 40 | -1.2632e-05 | 3.5486 | -9.5381e-07 | -0.00017573 | 4.8011 | 0 | 4.8009 |  | 15.2009 | 4 | 15.2009 | 70.0055 | 35.0027 | 15 | 35 | 0.0027341 | 0.044248 | 1.2632e-05 | 5.9613e-07 | 1 | 0
1288 | 21.4667 | 5 | 12 | 5 | 12 | 70.0053 | 40 | -1.3556e-05 | 3.5486 | -9.2373e-07 | -0.00018858 | 4.801 | 0 | 4.8008 |  | 15.2008 | 4 | 15.2008 | 70.0053 | 35.0026 | 15 | 35 | 0.0026366 | 0.046885 | 1.3556e-05 | 5.7733e-07 | 1 | 0
1289 | 21.4833 | 5 | 12 | 5 | 12 | 70.0051 | 40 | -1.4448e-05 | 3.5486 | -8.9275e-07 | -0.000201 | 4.801 | 0 | 4.8008 |  | 15.2008 | 4 | 15.2008 | 70.0051 | 35.0025 | 15 | 35 | 0.0025367 | 0.049421 | 1.4448e-05 | 5.5797e-07 | 1 | 0
1290 | 21.5 | 5 | 12 | 5 | 12 | 70.0049 | 40 | -1.5309e-05 | 3.5486 | -8.6093e-07 | -0.00021298 | 4.801 | 0 | 4.8008 |  | 15.2008 | 4 | 15.2008 | 70.0049 | 35.0024 | 15 | 35 | 0.0024345 | 0.051856 | 1.5309e-05 | 5.3808e-07 | 1 | 0
1291 | 21.5167 | 5 | 12 | 5 | 12 | 70.0047 | 40 | -1.6138e-05 | 3.5485 | -8.2831e-07 | -0.0002245 | 4.801 | 0 | 4.8007 |  | 15.2007 | 4 | 15.2007 | 70.0047 | 35.0023 | 15 | 35 | 0.0023303 | 0.054186 | 1.6138e-05 | 5.1769e-07 | 1 | 0
1292 | 21.5333 | 5 | 12 | 5 | 12 | 70.0044 | 40 | -1.6933e-05 | 3.5485 | -7.9495e-07 | -0.00023556 | 4.8009 | 0 | 4.8007 |  | 15.2007 | 4 | 15.2007 | 70.0044 | 35.0022 | 15 | 35 | 0.0022241 | 0.05641 | 1.6933e-05 | 4.9684e-07 | 1 | 0
1293 | 21.55 | 5 | 12 | 5 | 12 | 70.0042 | 40 | -1.7693e-05 | 3.5485 | -7.6091e-07 | -0.00024614 | 4.8009 | 0 | 4.8007 |  | 15.2007 | 4 | 15.2007 | 70.0042 | 35.0021 | 15 | 35 | 0.0021163 | 0.058527 | 1.7693e-05 | 4.7557e-07 | 1 | 0
1294 | 21.5667 | 5 | 12 | 5 | 12 | 70.004 | 40 | -1.842e-05 | 3.5485 | -7.2625e-07 | -0.00025625 | 4.8009 | 0 | 4.8006 |  | 15.2006 | 4 | 15.2006 | 70.004 | 35.002 | 15 | 35 | 0.0020068 | 0.060534 | 1.842e-05 | 4.5391e-07 | 1 | 0
1295 | 21.5833 | 5 | 12 | 5 | 12 | 70.0038 | 40 | -1.9111e-05 | 3.5485 | -6.9102e-07 | -0.00026586 | 4.8009 | 0 | 4.8006 |  | 15.2006 | 4 | 15.2006 | 70.0038 | 35.0019 | 15 | 35 | 0.001896 | 0.062429 | 1.9111e-05 | 4.3189e-07 | 1 | 0
1296 | 21.6 | 5 | 12 | 5 | 12 | 70.0036 | 40 | -1.9766e-05 | 3.5485 | -6.5529e-07 | -0.00027498 | 4.8008 | 0 | 4.8006 |  | 15.2006 | 4 | 15.2006 | 70.0036 | 35.0018 | 15 | 35 | 0.0017839 | 0.064213 | 1.9766e-05 | 4.0955e-07 | 1 | 0
1297 | 21.6167 | 5 | 12 | 5 | 12 | 70.0033 | 40 | -2.0385e-05 | 3.5484 | -6.1909e-07 | -0.00028359 | 4.8008 | 0 | 4.8005 |  | 15.2005 | 4 | 15.2005 | 70.0033 | 35.0017 | 15 | 35 | 0.0016708 | 0.065884 | 2.0385e-05 | 3.8693e-07 | 1 | 0
1298 | 21.6333 | 5 | 12 | 5 | 12 | 70.0031 | 40 | -2.0968e-05 | 3.5484 | -5.825e-07 | -0.00029169 | 4.8008 | 0 | 4.8005 |  | 15.2005 | 4 | 15.2005 | 70.0031 | 35.0016 | 15 | 35 | 0.0015568 | 0.067441 | 2.0968e-05 | 3.6406e-07 | 1 | 0
1299 | 21.65 | 5 | 12 | 5 | 12 | 70.0029 | 40 | -2.1513e-05 | 3.5484 | -5.4557e-07 | -0.00029928 | 4.8008 | 0 | 4.8005 |  | 15.2005 | 4 | 15.2005 | 70.0029 | 35.0014 | 15 | 35 | 0.0014422 | 0.068883 | 2.1513e-05 | 3.4098e-07 | 1 | 0
1300 | 21.6667 | 5 | 12 | 5 | 12 | 70.0027 | 40 | -2.2022e-05 | 3.5484 | -5.0836e-07 | -0.00030635 | 4.8007 | 0 | 4.8004 |  | 15.2004 | 4 | 15.2004 | 70.0027 | 35.0013 | 15 | 35 | 0.001327 | 0.07021 | 2.2022e-05 | 3.1772e-07 | 1 | 0
1301 | 21.6833 | 5 | 12 | 5 | 12 | 70.0024 | 40 | -2.2492e-05 | 3.5483 | -4.7091e-07 | -0.00031291 | 4.8007 | 0 | 4.8004 |  | 15.2004 | 4 | 15.2004 | 70.0024 | 35.0012 | 15 | 35 | 0.0012114 | 0.071422 | 2.2492e-05 | 2.9432e-07 | 1 | 0
1302 | 21.7 | 5 | 12 | 5 | 12 | 70.0022 | 40 | -2.2926e-05 | 3.5483 | -4.3329e-07 | -0.00031893 | 4.8007 | 0 | 4.8004 |  | 15.2004 | 4 | 15.2004 | 70.0022 | 35.0011 | 15 | 35 | 0.0010956 | 0.072517 | 2.2926e-05 | 2.7081e-07 | 1 | 0
1303 | 21.7167 | 5 | 12 | 5 | 12 | 70.002 | 40 | -2.3321e-05 | 3.5483 | -3.9556e-07 | -0.00032444 | 4.8006 | 0 | 4.8003 |  | 15.2003 | 4 | 15.2003 | 70.002 | 35.001 | 15 | 35 | 0.00097983 | 0.073497 | 2.3321e-05 | 2.4722e-07 | 1 | 0
1304 | 21.7333 | 5 | 12 | 5 | 12 | 70.0017 | 40 | -2.3679e-05 | 3.5483 | -3.5775e-07 | -0.00032941 | 4.8006 | 0 | 4.8003 |  | 15.2003 | 4 | 15.2003 | 70.0017 | 35.0009 | 15 | 35 | 0.00086416 | 0.074361 | 2.3679e-05 | 2.236e-07 | 1 | 0
1305 | 21.75 | 5 | 12 | 5 | 12 | 70.0015 | 40 | -2.3999e-05 | 3.5482 | -3.1994e-07 | -0.00033386 | 4.8006 | 0 | 4.8002 |  | 15.2002 | 4 | 15.2002 | 70.0015 | 35.0007 | 15 | 35 | 0.00074878 | 0.07511 | 2.3999e-05 | 1.9996e-07 | 1 | 0
1306 | 21.7667 | 5 | 12 | 5 | 12 | 70.0013 | 40 | -2.4281e-05 | 3.5482 | -2.8217e-07 | -0.00033779 | 4.8005 | 0 | 4.8002 |  | 15.2002 | 4 | 15.2002 | 70.0013 | 35.0006 | 15 | 35 | 0.00063386 | 0.075744 | 2.4281e-05 | 1.7636e-07 | 1 | 0
1307 | 21.7833 | 5 | 12 | 5 | 12 | 70.001 | 40 | -2.4526e-05 | 3.5482 | -2.445e-07 | -0.00034119 | 4.8005 | 0 | 4.8002 |  | 15.2002 | 4 | 15.2002 | 70.001 | 35.0005 | 15 | 35 | 0.00051953 | 0.076263 | 2.4526e-05 | 1.5281e-07 | 1 | 0
1308 | 21.8 | 5 | 12 | 5 | 12 | 70.0008 | 40 | -2.4733e-05 | 3.5482 | -2.0697e-07 | -0.00034407 | 4.8005 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0008 | 35.0004 | 15 | 35 | 0.00040597 | 0.076669 | 2.4733e-05 | 1.2936e-07 | 1 | 0
1309 | 21.8167 | 5 | 12 | 5 | 12 | 70.0006 | 40 | -2.4902e-05 | 3.5482 | -1.6964e-07 | -0.00034643 | 4.8004 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0006 | 35.0003 | 15 | 35 | 0.00029331 | 0.076963 | 2.4902e-05 | 1.0603e-07 | 1 | 0
1310 | 21.8333 | 5 | 12 | 5 | 12 | 70.0004 | 40 | -2.5035e-05 | 3.5481 | -1.3256e-07 | -0.00034827 | 4.8004 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0004 | 35.0002 | 15 | 35 | 0.0001817 | 0.077144 | 2.5035e-05 | 8.2851e-08 | 1 | 0
1311 | 21.85 | 5 | 12 | 5 | 12 | 70.0001 | 40 | -2.5131e-05 | 3.5481 | -9.5774e-08 | -0.00034961 | 4.8004 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35.0001 | 15 | 35 | 7.1284e-05 | 0.077216 | 2.5131e-05 | 5.9859e-08 | 1 | 0
1312 | 21.8667 | 5 | 12 | 5 | 12 | 69.9999 | 40 | -2.519e-05 | 3.5481 | -5.933e-08 | -0.00035043 | 4.8003 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 35 | 15 | 35 | -3.7797e-05 | 0.077178 | 2.519e-05 | 3.7081e-08 | 1 | 0
1313 | 21.8833 | 5 | 12 | 5 | 12 | 69.9997 | 40 | -2.5213e-05 | 3.5481 | -2.3276e-08 | -0.00035076 | 4.8003 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9997 | 34.9999 | 15 | 35 | -0.00014541 | 0.077032 | 2.5213e-05 | 1.4548e-08 | 1 | 0
1314 | 21.9 | 5 | 12 | 5 | 12 | 69.9995 | 40 | -2.5201e-05 | 3.548 | 1.2342e-08 | -0.00035058 | 4.8003 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9995 | 34.9997 | 15 | 35 | -0.00025142 | 0.076781 | 2.5201e-05 | -7.7137e-09 | -1 | -2
1315 | 21.9167 | 5 | 12 | 5 | 12 | 69.9993 | 40 | -2.5153e-05 | 3.548 | 4.7481e-08 | -0.00034992 | 4.8002 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9993 | 34.9996 | 15 | 35 | -0.0003557 | 0.076425 | 2.5153e-05 | -2.9675e-08 | -1 | 0
1316 | 21.9333 | 5 | 12 | 5 | 12 | 69.9991 | 40 | -2.5071e-05 | 3.548 | 8.2096e-08 | -0.00034878 | 4.8002 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9991 | 34.9995 | 15 | 35 | -0.00045813 | 0.075967 | 2.5071e-05 | -5.131e-08 | -1 | 0
1317 | 21.95 | 5 | 12 | 5 | 12 | 69.9989 | 40 | -2.4955e-05 | 3.548 | 1.1615e-07 | -0.00034717 | 4.8002 | 0 | 4.7998 |  | 15.1998 | 4 | 15.1998 | 69.9989 | 34.9994 | 15 | 35 | -0.00055859 | 0.075409 | 2.4955e-05 | -7.2593e-08 | -1 | 0
1318 | 21.9667 | 5 | 12 | 5 | 12 | 69.9987 | 40 | -2.4806e-05 | 3.5479 | 1.496e-07 | -0.00034508 | 4.8001 | 0 | 4.7998 |  | 15.1998 | 4 | 15.1998 | 69.9987 | 34.9993 | 15 | 35 | -0.00065697 | 0.074752 | 2.4806e-05 | -9.3497e-08 | -1 | 0
1319 | 21.9833 | 5 | 12 | 5 | 12 | 69.9985 | 40 | -2.4623e-05 | 3.5479 | 1.824e-07 | -0.00034255 | 4.8001 | 0 | 4.7998 |  | 15.1998 | 4 | 15.1998 | 69.9985 | 34.9992 | 15 | 35 | -0.00075314 | 0.073998 | 2.4623e-05 | -1.14e-07 | -1 | 0
1320 | 22 | 5 | 12 | 5 | 12 | 69.9983 | 40 | -2.4409e-05 | 3.5479 | 2.1452e-07 | -0.00033956 | 4.8001 | 0 | 4.7997 |  | 15.1997 | 4 | 15.1997 | 69.9983 | 34.9992 | 15 | 35 | -0.00084702 | 0.073151 | 2.4409e-05 | -1.3408e-07 | -1 | 0
1321 | 22.0167 | 5 | 12 | 5 | 12 | 69.9981 | 40 | -2.4163e-05 | 3.5479 | 2.4592e-07 | -0.00033614 | 4.8 | 0 | 4.7997 |  | 15.1997 | 4 | 15.1997 | 69.9981 | 34.9991 | 15 | 35 | -0.00093848 | 0.072213 | 2.4163e-05 | -1.537e-07 | -1 | 0
1322 | 22.0333 | 5 | 12 | 5 | 12 | 69.9979 | 40 | -2.3886e-05 | 3.5478 | 2.7658e-07 | -0.00033229 | 4.8 | 0 | 4.7997 |  | 15.1997 | 4 | 15.1997 | 69.9979 | 34.999 | 15 | 35 | -0.0010274 | 0.071185 | 2.3886e-05 | -1.7286e-07 | -1 | 0
1323 | 22.05 | 5 | 12 | 5 | 12 | 69.9978 | 40 | -2.358e-05 | 3.5478 | 3.0644e-07 | -0.00032803 | 4.8 | 0 | 4.7996 |  | 15.1996 | 4 | 15.1996 | 69.9978 | 34.9989 | 15 | 35 | -0.0011138 | 0.070072 | 2.358e-05 | -1.9153e-07 | -1 | 0
1324 | 22.0667 | 5 | 12 | 5 | 12 | 69.9976 | 40 | -2.3244e-05 | 3.5478 | 3.3549e-07 | -0.00032336 | 4.7999 | 0 | 4.7996 |  | 15.1996 | 4 | 15.1996 | 69.9976 | 34.9988 | 15 | 35 | -0.0011975 | 0.068874 | 2.3244e-05 | -2.0968e-07 | -1 | 0
1325 | 22.0833 | 5 | 12 | 5 | 12 | 69.9974 | 40 | -2.2881e-05 | 3.5478 | 3.637e-07 | -0.0003183 | 4.7999 | 0 | 4.7996 |  | 15.1996 | 4 | 15.1996 | 69.9974 | 34.9987 | 15 | 35 | -0.0012784 | 0.067596 | 2.2881e-05 | -2.2731e-07 | -1 | 0
1326 | 22.1 | 5 | 12 | 5 | 12 | 69.9973 | 40 | -2.249e-05 | 3.5477 | 3.9102e-07 | -0.00031286 | 4.7999 | 0 | 4.7996 |  | 15.1996 | 4 | 15.1996 | 69.9973 | 34.9986 | 15 | 35 | -0.0013565 | 0.066239 | 2.249e-05 | -2.4439e-07 | -1 | 0
1327 | 22.1167 | 5 | 12 | 5 | 12 | 69.9971 | 40 | -2.2072e-05 | 3.5477 | 4.1745e-07 | -0.00030706 | 4.7998 | 0 | 4.7995 |  | 15.1995 | 4 | 15.1995 | 69.9971 | 34.9986 | 15 | 35 | -0.0014317 | 0.064808 | 2.2072e-05 | -2.6091e-07 | -1 | 0
1328 | 22.1333 | 5 | 12 | 5 | 12 | 69.997 | 40 | -2.1629e-05 | 3.5477 | 4.4295e-07 | -0.00030089 | 4.7998 | 0 | 4.7995 |  | 15.1995 | 4 | 15.1995 | 69.997 | 34.9985 | 15 | 35 | -0.0015039 | 0.063304 | 2.1629e-05 | -2.7684e-07 | -1 | 0
1329 | 22.15 | 5 | 12 | 5 | 12 | 69.9969 | 40 | -2.1162e-05 | 3.5477 | 4.6749e-07 | -0.00029439 | 4.7998 | 0 | 4.7995 |  | 15.1995 | 4 | 15.1995 | 69.9969 | 34.9984 | 15 | 35 | -0.001573 | 0.061731 | 2.1162e-05 | -2.9218e-07 | -1 | 0
1330 | 22.1667 | 5 | 12 | 5 | 12 | 69.9967 | 40 | -2.0671e-05 | 3.5477 | 4.9106e-07 | -0.00028756 | 4.7998 | 0 | 4.7995 |  | 15.1995 | 4 | 15.1995 | 69.9967 | 34.9984 | 15 | 35 | -0.0016391 | 0.060092 | 2.0671e-05 | -3.0692e-07 | -1 | 0
1331 | 22.1833 | 5 | 12 | 5 | 12 | 69.9966 | 40 | -2.0157e-05 | 3.5476 | 5.1364e-07 | -0.00028041 | 4.7997 | 0 | 4.7995 |  | 15.1995 | 4 | 15.1995 | 69.9966 | 34.9983 | 15 | 35 | -0.001702 | 0.05839 | 2.0157e-05 | -3.2103e-07 | -1 | 0
1332 | 22.2 | 5 | 12 | 5 | 12 | 69.9965 | 40 | -1.9622e-05 | 3.5476 | 5.3521e-07 | -0.00027297 | 4.7997 | 0 | 4.7994 |  | 15.1994 | 4 | 15.1994 | 69.9965 | 34.9982 | 15 | 35 | -0.0017617 | 0.056628 | 1.9622e-05 | -3.3451e-07 | -1 | 0
1333 | 22.2167 | 5 | 12 | 5 | 12 | 69.9964 | 40 | -1.9066e-05 | 3.5476 | 5.5574e-07 | -0.00026524 | 4.7997 | 0 | 4.7994 |  | 15.1994 | 4 | 15.1994 | 69.9964 | 34.9982 | 15 | 35 | -0.0018181 | 0.05481 | 1.9066e-05 | -3.4734e-07 | -1 | 0
1334 | 22.2333 | 5 | 12 | 5 | 12 | 69.9963 | 40 | -1.8491e-05 | 3.5476 | 5.7524e-07 | -0.00025723 | 4.7997 | 0 | 4.7994 |  | 15.1994 | 4 | 15.1994 | 69.9963 | 34.9981 | 15 | 35 | -0.0018713 | 0.052938 | 1.8491e-05 | -3.5952e-07 | -1 | 0
1335 | 22.25 | 5 | 12 | 5 | 12 | 69.9962 | 40 | -1.7897e-05 | 3.5476 | 5.9367e-07 | -0.00024898 | 4.7996 | 0 | 4.7994 |  | 15.1994 | 4 | 15.1994 | 69.9962 | 34.9981 | 15 | 35 | -0.0019211 | 0.051017 | 1.7897e-05 | -3.7104e-07 | -1 | 0
1336 | 22.2667 | 5 | 12 | 5 | 12 | 69.9961 | 40 | -1.7286e-05 | 3.5475 | 6.1103e-07 | -0.00024048 | 4.7996 | 0 | 4.7994 |  | 15.1994 | 4 | 15.1994 | 69.9961 | 34.998 | 15 | 35 | -0.0019677 | 0.04905 | 1.7286e-05 | -3.8189e-07 | -1 | 0
1337 | 22.2833 | 5 | 12 | 5 | 12 | 69.996 | 40 | -1.6659e-05 | 3.5475 | 6.2731e-07 | -0.00023175 | 4.7996 | 0 | 4.7994 |  | 15.1994 | 4 | 15.1994 | 69.996 | 34.998 | 15 | 35 | -0.0020108 | 0.047039 | 1.6659e-05 | -3.9207e-07 | -1 | 0
1338 | 22.3 | 5 | 12 | 5 | 12 | 69.9959 | 40 | -1.6016e-05 | 3.5475 | 6.425e-07 | -0.00022281 | 4.7996 | 0 | 4.7993 |  | 15.1993 | 4 | 15.1993 | 69.9959 | 34.9979 | 15 | 35 | -0.0020506 | 0.044988 | 1.6016e-05 | -4.0156e-07 | -1 | 0
1339 | 22.3167 | 5 | 12 | 5 | 12 | 69.9958 | 40 | -1.536e-05 | 3.5475 | 6.5659e-07 | -0.00021368 | 4.7995 | 0 | 4.7993 |  | 15.1993 | 4 | 15.1993 | 69.9958 | 34.9979 | 15 | 35 | -0.002087 | 0.042901 | 1.536e-05 | -4.1037e-07 | -1 | 0
1340 | 22.3333 | 5 | 12 | 5 | 12 | 69.9958 | 40 | -1.469e-05 | 3.5475 | 6.6959e-07 | -0.00020436 | 4.7995 | 0 | 4.7993 |  | 15.1993 | 4 | 15.1993 | 69.9958 | 34.9979 | 15 | 35 | -0.00212 | 0.040781 | 1.469e-05 | -4.1849e-07 | -1 | 0
1341 | 22.35 | 5 | 12 | 5 | 12 | 69.9957 | 40 | -1.4009e-05 | 3.5475 | 6.8147e-07 | -0.00019488 | 4.7995 | 0 | 4.7993 |  | 15.1993 | 4 | 15.1993 | 69.9957 | 34.9979 | 15 | 35 | -0.0021496 | 0.038632 | 1.4009e-05 | -4.2592e-07 | -1 | 0
1342 | 22.3667 | 5 | 12 | 5 | 12 | 69.9956 | 40 | -1.3316e-05 | 3.5474 | 6.9224e-07 | -0.00018525 | 4.7995 | 0 | 4.7993 |  | 15.1993 | 4 | 15.1993 | 69.9956 | 34.9978 | 15 | 35 | -0.0021758 | 0.036456 | 1.3316e-05 | -4.3265e-07 | -1 | 0
1343 | 22.3833 | 5 | 12 | 5 | 12 | 69.9956 | 40 | -1.2614e-05 | 3.5474 | 7.0191e-07 | -0.00017549 | 4.7995 | 0 | 4.7993 |  | 15.1993 | 4 | 15.1993 | 69.9956 | 34.9978 | 15 | 35 | -0.0021986 | 0.034257 | 1.2614e-05 | -4.3869e-07 | -1 | 0
1344 | 22.4 | 5 | 12 | 5 | 12 | 69.9956 | 40 | -1.1904e-05 | 3.5474 | 7.1047e-07 | -0.0001656 | 4.7995 | 0 | 4.7993 |  | 15.1993 | 4 | 15.1993 | 69.9956 | 34.9978 | 15 | 35 | -0.0022181 | 0.032039 | 1.1904e-05 | -4.4404e-07 | -1 | 0
1345 | 22.4167 | 5 | 12 | 5 | 12 | 69.9955 | 40 | -1.1186e-05 | 3.5474 | 7.1792e-07 | -0.00015562 | 4.7994 | 0 | 4.7993 |  | 15.1993 | 4 | 15.1993 | 69.9955 | 34.9978 | 15 | 35 | -0.0022342 | 0.029805 | 1.1186e-05 | -4.487e-07 | -1 | 0
1346 | 22.4333 | 5 | 12 | 5 | 12 | 69.9955 | 40 | -1.0462e-05 | 3.5474 | 7.2427e-07 | -0.00014554 | 4.7994 | 0 | 4.7993 |  | 15.1993 | 4 | 15.1993 | 69.9955 | 34.9978 | 15 | 35 | -0.0022469 | 0.027558 | 1.0462e-05 | -4.5267e-07 | -1 | 0
1347 | 22.45 | 5 | 12 | 5 | 12 | 69.9955 | 40 | -9.7323e-06 | 3.5474 | 7.2952e-07 | -0.00013539 | 4.7994 | 0 | 4.7993 |  | 15.1993 | 4 | 15.1993 | 69.9955 | 34.9977 | 15 | 35 | -0.0022563 | 0.025302 | 9.7323e-06 | -4.5595e-07 | -1 | 0
1348 | 22.4667 | 5 | 12 | 5 | 12 | 69.9955 | 40 | -8.9986e-06 | 3.5474 | 7.3368e-07 | -0.00012518 | 4.7994 | 0 | 4.7993 |  | 15.1993 | 4 | 15.1993 | 69.9955 | 34.9977 | 15 | 35 | -0.0022625 | 0.023039 | 8.9986e-06 | -4.5855e-07 | -1 | 0
1349 | 22.4833 | 5 | 12 | 5 | 12 | 69.9955 | 40 | -8.2618e-06 | 3.5474 | 7.3676e-07 | -0.00011493 | 4.7994 | 0 | 4.7993 |  | 15.1993 | 4 | 15.1993 | 69.9955 | 34.9977 | 15 | 35 | -0.0022654 | 0.020774 | 8.2618e-06 | -4.6048e-07 | -1 | 0
1350 | 22.5 | 5 | 12 | 5 | 12 | 69.9955 | 40 | -7.523e-06 | 3.5474 | 7.3877e-07 | -0.00010466 | 4.7994 | 0 | 4.7993 |  | 15.1993 | 4 | 15.1993 | 69.9955 | 34.9977 | 15 | 35 | -0.0022651 | 0.018509 | 7.523e-06 | -4.6173e-07 | -1 | 0
1351 | 22.5167 | 5 | 12 | 5 | 12 | 69.9955 | 40 | -6.7833e-06 | 3.5474 | 7.3972e-07 | -9.4367e-05 | 4.7994 | 0 | 4.7993 |  | 15.1993 | 4 | 15.1993 | 69.9955 | 34.9977 | 15 | 35 | -0.0022616 | 0.016247 | 6.7833e-06 | -4.6232e-07 | -1 | 0
1352 | 22.5333 | 5 | 12 | 5 | 12 | 69.9955 | 40 | -6.0437e-06 | 3.5474 | 7.3961e-07 | -8.4077e-05 | 4.7994 | 0 | 4.7993 |  | 15.1993 | 4 | 15.1993 | 69.9955 | 34.9977 | 15 | 35 | -0.002255 | 0.013992 | 6.0437e-06 | -4.6226e-07 | -1 | 0
1353 | 22.55 | 5 | 12 | 5 | 12 | 69.9955 | 40 | -5.3052e-06 | 3.5473 | 7.3848e-07 | -7.3804e-05 | 4.7994 | 0 | 4.7993 |  | 15.1993 | 4 | 15.1993 | 69.9955 | 34.9978 | 15 | 35 | -0.0022453 | 0.011747 | 5.3052e-06 | -4.6155e-07 | -1 | 0
1354 | 22.5667 | 5 | 12 | 5 | 12 | 69.9955 | 40 | -4.5689e-06 | 3.5473 | 7.3632e-07 | -6.3561e-05 | 4.7993 | 0 | 4.7993 |  | 15.1993 | 4 | 15.1993 | 69.9955 | 34.9978 | 15 | 35 | -0.0022326 | 0.0095144 | 4.5689e-06 | -4.602e-07 | -1 | 0
1355 | 22.5833 | 5 | 12 | 5 | 12 | 69.9956 | 40 | -3.8357e-06 | 3.5473 | 7.3316e-07 | -5.3361e-05 | 4.7993 | 0 | 4.7993 |  | 15.1993 | 4 | 15.1993 | 69.9956 | 34.9978 | 15 | 35 | -0.002217 | 0.0072974 | 3.8357e-06 | -4.5823e-07 | -1 | 0
1356 | 22.6 | 5 | 12 | 5 | 12 | 69.9956 | 40 | -3.1067e-06 | 3.5473 | 7.2902e-07 | -4.3219e-05 | 4.7993 | 0 | 4.7993 |  | 15.1993 | 4 | 15.1993 | 69.9956 | 34.9978 | 15 | 35 | -0.0021984 | 0.005099 | 3.1067e-06 | -4.5564e-07 | -1 | 0
1357 | 22.6167 | 5 | 12 | 5 | 12 | 69.9956 | 40 | -2.3828e-06 | 3.5473 | 7.2391e-07 | -3.3149e-05 | 4.7993 | 0 | 4.7993 |  | 15.1993 | 4 | 15.1993 | 69.9956 | 34.9978 | 15 | 35 | -0.002177 | 0.002922 | 2.3828e-06 | -4.5244e-07 | -1 | 0
1358 | 22.6333 | 5 | 12 | 5 | 12 | 69.9957 | 40 | -1.665e-06 | 3.5473 | 7.1785e-07 | -2.3162e-05 | 4.7993 | 0 | 4.7993 |  | 15.1993 | 4 | 15.1993 | 69.9957 | 34.9978 | 15 | 35 | -0.0021528 | 0.00076912 | 1.665e-06 | -4.4865e-07 | -1 | 0
1359 | 22.65 | 5 | 12 | 5 | 12 | 69.9957 | 40 | -9.5411e-07 | 3.5473 | 7.1086e-07 | -1.3273e-05 | 4.7993 | 0 | 4.7993 |  | 15.1993 | 4 | 15.1993 | 69.9957 | 34.9979 | 15 | 35 | -0.002126 | -0.0013569 | 9.5411e-07 | -4.4429e-07 | -1 | 0
1360 | 22.6667 | 5 | 12 | 5 | 12 | 69.9958 | 40 | -2.5114e-07 | 3.5473 | 7.0297e-07 | -3.4938e-06 | 4.7993 | 0 | 4.7993 |  | 15.1993 | 4 | 15.1993 | 69.9958 | 34.9979 | 15 | 35 | -0.0020965 | -0.0034533 | 2.5114e-07 | -4.3936e-07 | -1 | 0
1361 | 22.6833 | 5 | 12 | 5 | 12 | 69.9959 | 40 | 4.4305e-07 | 3.5473 | 6.942e-07 | 6.1636e-06 | 4.7993 | 0 | 4.7993 |  | 15.1993 | 4 | 15.1993 | 69.9959 | 34.9979 | 15 | 35 | -0.0020644 | -0.0055177 | 4.4305e-07 | -4.3387e-07 | -1 | 0
1362 | 22.7 | 5 | 12 | 5 | 12 | 69.9959 | 40 | 1.1276e-06 | 3.5473 | 6.8456e-07 | 1.5687e-05 | 4.7993 | 0 | 4.7994 |  | 15.1994 | 4 | 15.1994 | 69.9959 | 34.998 | 15 | 35 | -0.0020299 | -0.0075476 | 1.1276e-06 | -4.2785e-07 | -1 | 0
1363 | 22.7167 | 5 | 12 | 5 | 12 | 69.996 | 40 | 1.8017e-06 | 3.5473 | 6.741e-07 | 2.5065e-05 | 4.7993 | 0 | 4.7994 |  | 15.1994 | 4 | 15.1994 | 69.996 | 34.998 | 15 | 35 | -0.001993 | -0.0095406 | 1.8017e-06 | -4.2131e-07 | -1 | 0
1364 | 22.7333 | 5 | 12 | 5 | 12 | 69.9961 | 40 | 2.4645e-06 | 3.5473 | 6.6282e-07 | 3.4286e-05 | 4.7993 | 0 | 4.7994 |  | 15.1994 | 4 | 15.1994 | 69.9961 | 34.998 | 15 | 35 | -0.0019537 | -0.011494 | 2.4645e-06 | -4.1426e-07 | -1 | 0
1365 | 22.75 | 5 | 12 | 5 | 12 | 69.9962 | 40 | 3.1153e-06 | 3.5473 | 6.5077e-07 | 4.3339e-05 | 4.7993 | 0 | 4.7994 |  | 15.1994 | 4 | 15.1994 | 69.9962 | 34.9981 | 15 | 35 | -0.0019123 | -0.013407 | 3.1153e-06 | -4.0673e-07 | -1 | 0
1366 | 22.7667 | 5 | 12 | 5 | 12 | 69.9963 | 40 | 3.7533e-06 | 3.5473 | 6.3795e-07 | 5.2214e-05 | 4.7993 | 0 | 4.7994 |  | 15.1994 | 4 | 15.1994 | 69.9963 | 34.9981 | 15 | 35 | -0.0018687 | -0.015275 | 3.7533e-06 | -3.9872e-07 | -1 | 0
1367 | 22.7833 | 5 | 12 | 5 | 12 | 69.9964 | 40 | 4.3777e-06 | 3.5473 | 6.2442e-07 | 6.09e-05 | 4.7994 | 0 | 4.7994 |  | 15.1994 | 4 | 15.1994 | 69.9964 | 34.9982 | 15 | 35 | -0.001823 | -0.017098 | 4.3777e-06 | -3.9026e-07 | -1 | 0
1368 | 22.8 | 5 | 12 | 5 | 12 | 69.9964 | 40 | 4.9879e-06 | 3.5474 | 6.1018e-07 | 6.9389e-05 | 4.7994 | 0 | 4.7994 |  | 15.1994 | 4 | 15.1994 | 69.9964 | 34.9982 | 15 | 35 | -0.0017754 | -0.018874 | 4.9879e-06 | -3.8136e-07 | -1 | 0
1369 | 22.8167 | 5 | 12 | 5 | 12 | 69.9965 | 40 | 5.5831e-06 | 3.5474 | 5.9527e-07 | 7.767e-05 | 4.7994 | 0 | 4.7994 |  | 15.1994 | 4 | 15.1994 | 69.9965 | 34.9983 | 15 | 35 | -0.0017259 | -0.0206 | 5.5831e-06 | -3.7204e-07 | -1 | 0
1370 | 22.8333 | 5 | 12 | 5 | 12 | 69.9967 | 40 | 6.1628e-06 | 3.5474 | 5.7972e-07 | 8.5735e-05 | 4.7994 | 0 | 4.7995 |  | 15.1995 | 4 | 15.1995 | 69.9967 | 34.9983 | 15 | 35 | -0.0016747 | -0.022274 | 6.1628e-06 | -3.6233e-07 | -1 | 0
1371 | 22.85 | 5 | 12 | 5 | 12 | 69.9968 | 40 | 6.7264e-06 | 3.5474 | 5.6357e-07 | 9.3575e-05 | 4.7994 | 0 | 4.7995 |  | 15.1995 | 4 | 15.1995 | 69.9968 | 34.9984 | 15 | 35 | -0.0016217 | -0.023896 | 6.7264e-06 | -3.5223e-07 | -1 | 0
1372 | 22.8667 | 5 | 12 | 5 | 12 | 69.9969 | 40 | 7.2732e-06 | 3.5474 | 5.4683e-07 | 0.00010118 | 4.7994 | 0 | 4.7995 |  | 15.1995 | 4 | 15.1995 | 69.9969 | 34.9984 | 15 | 35 | -0.0015672 | -0.025463 | 7.2732e-06 | -3.4177e-07 | -1 | 0
1373 | 22.8833 | 5 | 12 | 5 | 12 | 69.997 | 40 | 7.8028e-06 | 3.5474 | 5.2954e-07 | 0.00010855 | 4.7994 | 0 | 4.7995 |  | 15.1995 | 4 | 15.1995 | 69.997 | 34.9985 | 15 | 35 | -0.0015112 | -0.026974 | 7.8028e-06 | -3.3096e-07 | -1 | 0
1374 | 22.9 | 5 | 12 | 5 | 12 | 69.9971 | 40 | 8.3145e-06 | 3.5474 | 5.1174e-07 | 0.00011567 | 4.7994 | 0 | 4.7995 |  | 15.1995 | 4 | 15.1995 | 69.9971 | 34.9985 | 15 | 35 | -0.0014538 | -0.028428 | 8.3145e-06 | -3.1984e-07 | -1 | 0
1375 | 22.9167 | 5 | 12 | 5 | 12 | 69.9972 | 40 | 8.808e-06 | 3.5474 | 4.9345e-07 | 0.00012253 | 4.7994 | 0 | 4.7996 |  | 15.1996 | 4 | 15.1996 | 69.9972 | 34.9986 | 15 | 35 | -0.0013951 | -0.029823 | 8.808e-06 | -3.0841e-07 | -1 | 0
1376 | 22.9333 | 5 | 12 | 5 | 12 | 69.9973 | 40 | 9.2827e-06 | 3.5474 | 4.7471e-07 | 0.00012914 | 4.7994 | 0 | 4.7996 |  | 15.1996 | 4 | 15.1996 | 69.9973 | 34.9987 | 15 | 35 | -0.0013352 | -0.031158 | 9.2827e-06 | -2.9669e-07 | -1 | 0
1377 | 22.95 | 5 | 12 | 5 | 12 | 69.9975 | 40 | 9.7382e-06 | 3.5474 | 4.5554e-07 | 0.00013547 | 4.7995 | 0 | 4.7996 |  | 15.1996 | 4 | 15.1996 | 69.9975 | 34.9987 | 15 | 35 | -0.0012742 | -0.032433 | 9.7382e-06 | -2.8471e-07 | -1 | 0
1378 | 22.9667 | 5 | 12 | 5 | 12 | 69.9976 | 40 | 1.0174e-05 | 3.5474 | 4.3599e-07 | 0.00014154 | 4.7995 | 0 | 4.7996 |  | 15.1996 | 4 | 15.1996 | 69.9976 | 34.9988 | 15 | 35 | -0.0012123 | -0.033645 | 1.0174e-05 | -2.7249e-07 | -1 | 0
1379 | 22.9833 | 5 | 12 | 5 | 12 | 69.9977 | 40 | 1.059e-05 | 3.5474 | 4.1608e-07 | 0.00014733 | 4.7995 | 0 | 4.7996 |  | 15.1996 | 4 | 15.1996 | 69.9977 | 34.9989 | 15 | 35 | -0.0011494 | -0.034794 | 1.059e-05 | -2.6005e-07 | -1 | 0
1380 | 23 | 5 | 12 | 5 | 12 | 69.9978 | 40 | 1.0986e-05 | 3.5475 | 3.9584e-07 | 0.00015283 | 4.7995 | 0 | 4.7997 |  | 15.1997 | 4 | 15.1997 | 69.9978 | 34.9989 | 15 | 35 | -0.0010857 | -0.03588 | 1.0986e-05 | -2.474e-07 | -1 | 0
1381 | 23.0167 | 5 | 12 | 5 | 12 | 69.998 | 40 | 1.1361e-05 | 3.5475 | 3.7531e-07 | 0.00015806 | 4.7995 | 0 | 4.7997 |  | 15.1997 | 4 | 15.1997 | 69.998 | 34.999 | 15 | 35 | -0.0010214 | -0.036902 | 1.1361e-05 | -2.3457e-07 | -1 | 0
1382 | 23.0333 | 5 | 12 | 5 | 12 | 69.9981 | 40 | 1.1716e-05 | 3.5475 | 3.5453e-07 | 0.00016299 | 4.7995 | 0 | 4.7997 |  | 15.1997 | 4 | 15.1997 | 69.9981 | 34.999 | 15 | 35 | -0.00095644 | -0.037858 | 1.1716e-05 | -2.2158e-07 | -1 | 0
1383 | 23.05 | 5 | 12 | 5 | 12 | 69.9982 | 40 | 1.2049e-05 | 3.5475 | 3.3352e-07 | 0.00016763 | 4.7995 | 0 | 4.7997 |  | 15.1997 | 4 | 15.1997 | 69.9982 | 34.9991 | 15 | 35 | -0.000891 | -0.038749 | 1.2049e-05 | -2.0845e-07 | -1 | 0
1384 | 23.0667 | 5 | 12 | 5 | 12 | 69.9983 | 40 | 1.2362e-05 | 3.5475 | 3.1231e-07 | 0.00017197 | 4.7996 | 0 | 4.7997 |  | 15.1997 | 4 | 15.1997 | 69.9983 | 34.9992 | 15 | 35 | -0.00082516 | -0.039574 | 1.2362e-05 | -1.9519e-07 | -1 | 0
1385 | 23.0833 | 5 | 12 | 5 | 12 | 69.9985 | 40 | 1.2653e-05 | 3.5475 | 2.9094e-07 | 0.00017602 | 4.7996 | 0 | 4.7998 |  | 15.1998 | 4 | 15.1998 | 69.9985 | 34.9992 | 15 | 35 | -0.00075902 | -0.040333 | 1.2653e-05 | -1.8184e-07 | -1 | 0
1386 | 23.1 | 5 | 12 | 5 | 12 | 69.9986 | 40 | 1.2922e-05 | 3.5475 | 2.6944e-07 | 0.00017977 | 4.7996 | 0 | 4.7998 |  | 15.1998 | 4 | 15.1998 | 69.9986 | 34.9993 | 15 | 35 | -0.00069267 | -0.041026 | 1.2922e-05 | -1.684e-07 | -1 | 0
1387 | 23.1167 | 5 | 12 | 5 | 12 | 69.9987 | 40 | 1.317e-05 | 3.5475 | 2.4784e-07 | 0.00018322 | 4.7996 | 0 | 4.7998 |  | 15.1998 | 4 | 15.1998 | 69.9987 | 34.9994 | 15 | 35 | -0.00062621 | -0.041652 | 1.317e-05 | -1.549e-07 | -1 | 0
1388 | 23.1333 | 5 | 12 | 5 | 12 | 69.9989 | 40 | 1.3396e-05 | 3.5476 | 2.2618e-07 | 0.00018636 | 4.7996 | 0 | 4.7998 |  | 15.1998 | 4 | 15.1998 | 69.9989 | 34.9994 | 15 | 35 | -0.00055974 | -0.042212 | 1.3396e-05 | -1.4136e-07 | -1 | 0
1389 | 23.15 | 5 | 12 | 5 | 12 | 69.999 | 40 | 1.3601e-05 | 3.5476 | 2.0448e-07 | 0.00018921 | 4.7997 | 0 | 4.7998 |  | 15.1998 | 4 | 15.1998 | 69.999 | 34.9995 | 15 | 35 | -0.00049335 | -0.042705 | 1.3601e-05 | -1.278e-07 | -1 | 0
1390 | 23.1667 | 5 | 12 | 5 | 12 | 69.9991 | 40 | 1.3783e-05 | 3.5476 | 1.8277e-07 | 0.00019175 | 4.7997 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9991 | 34.9996 | 15 | 35 | -0.00042713 | -0.043132 | 1.3783e-05 | -1.1423e-07 | -1 | 0
1391 | 23.1833 | 5 | 12 | 5 | 12 | 69.9993 | 40 | 1.3945e-05 | 3.5476 | 1.6109e-07 | 0.00019399 | 4.7997 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9993 | 34.9996 | 15 | 35 | -0.00036117 | -0.043493 | 1.3945e-05 | -1.0068e-07 | -1 | 0
1392 | 23.2 | 5 | 12 | 5 | 12 | 69.9994 | 40 | 1.4084e-05 | 3.5476 | 1.3947e-07 | 0.00019593 | 4.7997 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9994 | 34.9997 | 15 | 35 | -0.00029556 | -0.043789 | 1.4084e-05 | -8.7169e-08 | -1 | 0
1393 | 23.2167 | 5 | 12 | 5 | 12 | 69.9995 | 40 | 1.4202e-05 | 3.5476 | 1.1793e-07 | 0.00019757 | 4.7997 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9995 | 34.9998 | 15 | 35 | -0.00023039 | -0.044019 | 1.4202e-05 | -7.3708e-08 | -1 | 0
1394 | 23.2333 | 5 | 12 | 5 | 12 | 69.9997 | 40 | 1.4298e-05 | 3.5476 | 9.6509e-08 | 0.00019891 | 4.7997 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9997 | 34.9998 | 15 | 35 | -0.00016574 | -0.044185 | 1.4298e-05 | -6.0318e-08 | -1 | 0
1395 | 23.25 | 5 | 12 | 5 | 12 | 69.9998 | 40 | 1.4374e-05 | 3.5477 | 7.5228e-08 | 0.00019996 | 4.7998 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9998 | 34.9999 | 15 | 35 | -0.0001017 | -0.044287 | 1.4374e-05 | -4.7017e-08 | -1 | 0
1396 | 23.2667 | 5 | 12 | 5 | 12 | 69.9999 | 40 | 1.4428e-05 | 3.5477 | 5.4118e-08 | 0.00020071 | 4.7998 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 35 | 15 | 35 | -3.8343e-05 | -0.044325 | 1.4428e-05 | -3.3824e-08 | -1 | 0
1397 | 23.2833 | 5 | 12 | 5 | 12 | 70 | 40 | 1.4461e-05 | 3.5477 | 3.3207e-08 | 0.00020117 | 4.7998 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | 2.4241e-05 | -0.044301 | 1.4461e-05 | -2.0754e-08 | -1 | 0
1398 | 23.3 | 5 | 12 | 5 | 12 | 70.0002 | 40 | 1.4474e-05 | 3.5477 | 1.252e-08 | 0.00020135 | 4.7998 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0002 | 35.0001 | 15 | 35 | 8.5978e-05 | -0.044215 | 1.4474e-05 | -7.8251e-09 | -1 | 0
1399 | 23.3167 | 5 | 12 | 5 | 12 | 70.0003 | 40 | 1.4466e-05 | 3.5477 | -7.9153e-09 | 0.00020124 | 4.7998 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0003 | 35.0001 | 15 | 35 | 0.00014679 | -0.044068 | 1.4466e-05 | 4.9471e-09 | 1 | 2
1400 | 23.3333 | 5 | 12 | 5 | 12 | 70.0004 | 40 | 1.4438e-05 | 3.5477 | -2.8074e-08 | 0.00020085 | 4.7999 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0004 | 35.0002 | 15 | 35 | 0.00020661 | -0.043861 | 1.4438e-05 | 1.7547e-08 | 1 | 0
1401 | 23.35 | 5 | 12 | 5 | 12 | 70.0005 | 40 | 1.439e-05 | 3.5477 | -4.7933e-08 | 0.00020018 | 4.7999 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0005 | 35.0003 | 15 | 35 | 0.00026537 | -0.043596 | 1.439e-05 | 2.9958e-08 | 1 | 0
1402 | 23.3667 | 5 | 12 | 5 | 12 | 70.0006 | 40 | 1.4322e-05 | 3.5478 | -6.7466e-08 | 0.00019924 | 4.7999 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0006 | 35.0003 | 15 | 35 | 0.00032299 | -0.043273 | 1.4322e-05 | 4.2166e-08 | 1 | 0
1403 | 23.3833 | 5 | 12 | 5 | 12 | 70.0008 | 40 | 1.4235e-05 | 3.5478 | -8.6651e-08 | 0.00019804 | 4.7999 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0008 | 35.0004 | 15 | 35 | 0.00037941 | -0.042894 | 1.4235e-05 | 5.4157e-08 | 1 | 0
1404 | 23.4 | 5 | 12 | 5 | 12 | 70.0009 | 40 | 1.413e-05 | 3.5478 | -1.0547e-07 | 0.00019657 | 4.7999 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0009 | 35.0004 | 15 | 35 | 0.00043456 | -0.042459 | 1.413e-05 | 6.5916e-08 | 1 | 0
1405 | 23.4167 | 5 | 12 | 5 | 12 | 70.001 | 40 | 1.4006e-05 | 3.5478 | -1.2389e-07 | 0.00019485 | 4.8 | 0 | 4.8002 |  | 15.2002 | 4 | 15.2002 | 70.001 | 35.0005 | 15 | 35 | 0.0004884 | -0.041971 | 1.4006e-05 | 7.743e-08 | 1 | 0
1406 | 23.4333 | 5 | 12 | 5 | 12 | 70.0011 | 40 | 1.3864e-05 | 3.5478 | -1.419e-07 | 0.00019287 | 4.8 | 0 | 4.8002 |  | 15.2002 | 4 | 15.2002 | 70.0011 | 35.0005 | 15 | 35 | 0.00054084 | -0.04143 | 1.3864e-05 | 8.8687e-08 | 1 | 0
1407 | 23.45 | 5 | 12 | 5 | 12 | 70.0012 | 40 | 1.3705e-05 | 3.5478 | -1.5948e-07 | 0.00019065 | 4.8 | 0 | 4.8002 |  | 15.2002 | 4 | 15.2002 | 70.0012 | 35.0006 | 15 | 35 | 0.00059185 | -0.040838 | 1.3705e-05 | 9.9673e-08 | 1 | 0
1408 | 23.4667 | 5 | 12 | 5 | 12 | 70.0013 | 40 | 1.3528e-05 | 3.5478 | -1.766e-07 | 0.0001882 | 4.8 | 0 | 4.8002 |  | 15.2002 | 4 | 15.2002 | 70.0013 | 35.0006 | 15 | 35 | 0.00064137 | -0.040197 | 1.3528e-05 | 1.1038e-07 | 1 | 0
1409 | 23.4833 | 5 | 12 | 5 | 12 | 70.0014 | 40 | 1.3335e-05 | 3.5479 | -1.9326e-07 | 0.00018551 | 4.8 | 0 | 4.8002 |  | 15.2002 | 4 | 15.2002 | 70.0014 | 35.0007 | 15 | 35 | 0.00068935 | -0.039507 | 1.3335e-05 | 1.2079e-07 | 1 | 0
1410 | 23.5 | 5 | 12 | 5 | 12 | 70.0015 | 40 | 1.3125e-05 | 3.5479 | -2.0943e-07 | 0.0001826 | 4.8001 | 0 | 4.8002 |  | 15.2002 | 4 | 15.2002 | 70.0015 | 35.0007 | 15 | 35 | 0.00073574 | -0.038772 | 1.3125e-05 | 1.3089e-07 | 1 | 0
1411 | 23.5167 | 5 | 12 | 5 | 12 | 70.0016 | 40 | 1.29e-05 | 3.5479 | -2.2509e-07 | 0.00017946 | 4.8001 | 0 | 4.8002 |  | 15.2002 | 4 | 15.2002 | 70.0016 | 35.0008 | 15 | 35 | 0.0007805 | -0.037991 | 1.29e-05 | 1.4068e-07 | 1 | 0
1412 | 23.5333 | 5 | 12 | 5 | 12 | 70.0016 | 40 | 1.266e-05 | 3.5479 | -2.4024e-07 | 0.00017612 | 4.8001 | 0 | 4.8003 |  | 15.2003 | 4 | 15.2003 | 70.0016 | 35.0008 | 15 | 35 | 0.00082358 | -0.037168 | 1.266e-05 | 1.5015e-07 | 1 | 0
1413 | 23.55 | 5 | 12 | 5 | 12 | 70.0017 | 40 | 1.2405e-05 | 3.5479 | -2.5486e-07 | 0.00017258 | 4.8001 | 0 | 4.8003 |  | 15.2003 | 4 | 15.2003 | 70.0017 | 35.0009 | 15 | 35 | 0.00086495 | -0.036303 | 1.2405e-05 | 1.5928e-07 | 1 | 0
1414 | 23.5667 | 5 | 12 | 5 | 12 | 70.0018 | 40 | 1.2136e-05 | 3.5479 | -2.6892e-07 | 0.00016884 | 4.8001 | 0 | 4.8003 |  | 15.2003 | 4 | 15.2003 | 70.0018 | 35.0009 | 15 | 35 | 0.00090457 | -0.035398 | 1.2136e-05 | 1.6808e-07 | 1 | 0
1415 | 23.5833 | 5 | 12 | 5 | 12 | 70.0019 | 40 | 1.1854e-05 | 3.5479 | -2.8243e-07 | 0.00016491 | 4.8001 | 0 | 4.8003 |  | 15.2003 | 4 | 15.2003 | 70.0019 | 35.0009 | 15 | 35 | 0.00094241 | -0.034456 | 1.1854e-05 | 1.7652e-07 | 1 | 0
1416 | 23.6 | 5 | 12 | 5 | 12 | 70.002 | 40 | 1.1559e-05 | 3.5479 | -2.9537e-07 | 0.0001608 | 4.8002 | 0 | 4.8003 |  | 15.2003 | 4 | 15.2003 | 70.002 | 35.001 | 15 | 35 | 0.00097843 | -0.033477 | 1.1559e-05 | 1.8461e-07 | 1 | 0
1417 | 23.6167 | 5 | 12 | 5 | 12 | 70.002 | 40 | 1.1251e-05 | 3.5479 | -3.0772e-07 | 0.00015652 | 4.8002 | 0 | 4.8003 |  | 15.2003 | 4 | 15.2003 | 70.002 | 35.001 | 15 | 35 | 0.0010126 | -0.032465 | 1.1251e-05 | 1.9233e-07 | 1 | 0
1418 | 23.6333 | 5 | 12 | 5 | 12 | 70.0021 | 40 | 1.0931e-05 | 3.548 | -3.1949e-07 | 0.00015207 | 4.8002 | 0 | 4.8003 |  | 15.2003 | 4 | 15.2003 | 70.0021 | 35.001 | 15 | 35 | 0.001045 | -0.03142 | 1.0931e-05 | 1.9968e-07 | 1 | 0
1419 | 23.65 | 5 | 12 | 5 | 12 | 70.0022 | 40 | 1.0601e-05 | 3.548 | -3.3065e-07 | 0.00014747 | 4.8002 | 0 | 4.8003 |  | 15.2003 | 4 | 15.2003 | 70.0022 | 35.0011 | 15 | 35 | 0.0010754 | -0.030344 | 1.0601e-05 | 2.0666e-07 | 1 | 0
1420 | 23.6667 | 5 | 12 | 5 | 12 | 70.0022 | 40 | 1.0259e-05 | 3.548 | -3.4121e-07 | 0.00014273 | 4.8002 | 0 | 4.8004 |  | 15.2004 | 4 | 15.2004 | 70.0022 | 35.0011 | 15 | 35 | 0.0011039 | -0.02924 | 1.0259e-05 | 2.1326e-07 | 1 | 0
1421 | 23.6833 | 5 | 12 | 5 | 12 | 70.0023 | 40 | 9.9083e-06 | 3.548 | -3.5115e-07 | 0.00013784 | 4.8002 | 0 | 4.8004 |  | 15.2004 | 4 | 15.2004 | 70.0023 | 35.0011 | 15 | 35 | 0.0011306 | -0.02811 | 9.9083e-06 | 2.1947e-07 | 1 | 0
1422 | 23.7 | 5 | 12 | 5 | 12 | 70.0023 | 40 | 9.5478e-06 | 3.548 | -3.6047e-07 | 0.00013283 | 4.8002 | 0 | 4.8004 |  | 15.2004 | 4 | 15.2004 | 70.0023 | 35.0012 | 15 | 35 | 0.0011553 | -0.026954 | 9.5478e-06 | 2.2529e-07 | 1 | 0
1423 | 23.7167 | 5 | 12 | 5 | 12 | 70.0024 | 40 | 9.1787e-06 | 3.548 | -3.6916e-07 | 0.00012769 | 4.8002 | 0 | 4.8004 |  | 15.2004 | 4 | 15.2004 | 70.0024 | 35.0012 | 15 | 35 | 0.001178 | -0.025776 | 9.1787e-06 | 2.3073e-07 | 1 | 0
1424 | 23.7333 | 5 | 12 | 5 | 12 | 70.0024 | 40 | 8.8015e-06 | 3.548 | -3.7723e-07 | 0.00012244 | 4.8003 | 0 | 4.8004 |  | 15.2004 | 4 | 15.2004 | 70.0024 | 35.0012 | 15 | 35 | 0.0011988 | -0.024578 | 8.8015e-06 | 2.3577e-07 | 1 | 0
1425 | 23.75 | 5 | 12 | 5 | 12 | 70.0024 | 40 | 8.4168e-06 | 3.548 | -3.8466e-07 | 0.00011709 | 4.8003 | 0 | 4.8004 |  | 15.2004 | 4 | 15.2004 | 70.0024 | 35.0012 | 15 | 35 | 0.0012177 | -0.02336 | 8.4168e-06 | 2.4041e-07 | 1 | 0
1426 | 23.7667 | 5 | 12 | 5 | 12 | 70.0025 | 40 | 8.0253e-06 | 3.548 | -3.9146e-07 | 0.00011164 | 4.8003 | 0 | 4.8004 |  | 15.2004 | 4 | 15.2004 | 70.0025 | 35.0012 | 15 | 35 | 0.0012346 | -0.022125 | 8.0253e-06 | 2.4466e-07 | 1 | 0
1427 | 23.7833 | 5 | 12 | 5 | 12 | 70.0025 | 40 | 7.6277e-06 | 3.548 | -3.9761e-07 | 0.00010611 | 4.8003 | 0 | 4.8004 |  | 15.2004 | 4 | 15.2004 | 70.0025 | 35.0012 | 15 | 35 | 0.0012496 | -0.020876 | 7.6277e-06 | 2.4851e-07 | 1 | 0
1428 | 23.8 | 5 | 12 | 5 | 12 | 70.0025 | 40 | 7.2246e-06 | 3.5481 | -4.0314e-07 | 0.00010051 | 4.8003 | 0 | 4.8004 |  | 15.2004 | 4 | 15.2004 | 70.0025 | 35.0013 | 15 | 35 | 0.0012626 | -0.019613 | 7.2246e-06 | 2.5196e-07 | 1 | 0
1429 | 23.8167 | 5 | 12 | 5 | 12 | 70.0025 | 40 | 6.8166e-06 | 3.5481 | -4.0802e-07 | 9.4829e-05 | 4.8003 | 0 | 4.8004 |  | 15.2004 | 4 | 15.2004 | 70.0025 | 35.0013 | 15 | 35 | 0.0012737 | -0.018339 | 6.8166e-06 | 2.5501e-07 | 1 | 0
1430 | 23.8333 | 5 | 12 | 5 | 12 | 70.0026 | 40 | 6.4043e-06 | 3.5481 | -4.1227e-07 | 8.9094e-05 | 4.8003 | 0 | 4.8004 |  | 15.2004 | 4 | 15.2004 | 70.0026 | 35.0013 | 15 | 35 | 0.0012828 | -0.017057 | 6.4043e-06 | 2.5767e-07 | 1 | 0
1431 | 23.85 | 5 | 12 | 5 | 12 | 70.0026 | 40 | 5.9884e-06 | 3.5481 | -4.1589e-07 | 8.3308e-05 | 4.8003 | 0 | 4.8004 |  | 15.2004 | 4 | 15.2004 | 70.0026 | 35.0013 | 15 | 35 | 0.0012901 | -0.015767 | 5.9884e-06 | 2.5993e-07 | 1 | 0
1432 | 23.8667 | 5 | 12 | 5 | 12 | 70.0026 | 40 | 5.5695e-06 | 3.5481 | -4.1888e-07 | 7.7481e-05 | 4.8003 | 0 | 4.8004 |  | 15.2004 | 4 | 15.2004 | 70.0026 | 35.0013 | 15 | 35 | 0.0012954 | -0.014471 | 5.5695e-06 | 2.618e-07 | 1 | 0
1433 | 23.8833 | 5 | 12 | 5 | 12 | 70.0026 | 40 | 5.1483e-06 | 3.5481 | -4.2125e-07 | 7.162e-05 | 4.8003 | 0 | 4.8004 |  | 15.2004 | 4 | 15.2004 | 70.0026 | 35.0013 | 15 | 35 | 0.0012989 | -0.013172 | 5.1483e-06 | 2.6328e-07 | 1 | 0
1434 | 23.9 | 5 | 12 | 5 | 12 | 70.0026 | 40 | 4.7253e-06 | 3.5481 | -4.2299e-07 | 6.5736e-05 | 4.8004 | 0 | 4.8004 |  | 15.2004 | 4 | 15.2004 | 70.0026 | 35.0013 | 15 | 35 | 0.0013004 | -0.011872 | 4.7253e-06 | 2.6437e-07 | 1 | 0
1435 | 23.9167 | 5 | 12 | 5 | 12 | 70.0026 | 40 | 4.3012e-06 | 3.5481 | -4.2412e-07 | 5.9836e-05 | 4.8004 | 0 | 4.8004 |  | 15.2004 | 4 | 15.2004 | 70.0026 | 35.0013 | 15 | 35 | 0.0013002 | -0.010572 | 4.3012e-06 | 2.6507e-07 | 1 | 0
1436 | 23.9333 | 5 | 12 | 5 | 12 | 70.0026 | 40 | 3.8765e-06 | 3.5481 | -4.2464e-07 | 5.3928e-05 | 4.8004 | 0 | 4.8004 |  | 15.2004 | 4 | 15.2004 | 70.0026 | 35.0013 | 15 | 35 | 0.0012981 | -0.0092735 | 3.8765e-06 | 2.654e-07 | 1 | 0
1437 | 23.95 | 5 | 12 | 5 | 12 | 70.0026 | 40 | 3.452e-06 | 3.5481 | -4.2455e-07 | 4.8022e-05 | 4.8004 | 0 | 4.8004 |  | 15.2004 | 4 | 15.2004 | 70.0026 | 35.0013 | 15 | 35 | 0.0012943 | -0.0079793 | 3.452e-06 | 2.6535e-07 | 1 | 0
1438 | 23.9667 | 5 | 12 | 5 | 12 | 70.0026 | 40 | 3.0281e-06 | 3.5481 | -4.2388e-07 | 4.2126e-05 | 4.8004 | 0 | 4.8004 |  | 15.2004 | 4 | 15.2004 | 70.0026 | 35.0013 | 15 | 35 | 0.0012886 | -0.0066906 | 3.0281e-06 | 2.6492e-07 | 1 | 0
1439 | 23.9833 | 5 | 12 | 5 | 12 | 70.0026 | 40 | 2.6055e-06 | 3.5481 | -4.2262e-07 | 3.6246e-05 | 4.8004 | 0 | 4.8004 |  | 15.2004 | 4 | 15.2004 | 70.0026 | 35.0013 | 15 | 35 | 0.0012813 | -0.0054094 | 2.6055e-06 | 2.6413e-07 | 1 | 0
1440 | 24 | 5 | 12 | 5 | 12 | 70.0025 | 40 | 2.1847e-06 | 3.5481 | -4.2078e-07 | 3.0393e-05 | 4.8004 | 0 | 4.8004 |  | 15.2004 | 4 | 15.2004 | 70.0025 | 35.0013 | 15 | 35 | 0.0012722 | -0.0041371 | 2.1847e-06 | 2.6299e-07 | 1 | 0
1441 | 24.0167 | 5 | 12 | 5 | 12 | 70.0025 | 40 | 1.7663e-06 | 3.5481 | -4.1838e-07 | 2.4572e-05 | 4.8004 | 0 | 4.8004 |  | 15.2004 | 4 | 15.2004 | 70.0025 | 35.0013 | 15 | 35 | 0.0012615 | -0.0028756 | 1.7663e-06 | 2.6149e-07 | 1 | 0
1442 | 24.0333 | 5 | 12 | 5 | 12 | 70.0025 | 40 | 1.3509e-06 | 3.5481 | -4.1542e-07 | 1.8793e-05 | 4.8004 | 0 | 4.8004 |  | 15.2004 | 4 | 15.2004 | 70.0025 | 35.0012 | 15 | 35 | 0.0012492 | -0.0016265 | 1.3509e-06 | 2.5964e-07 | 1 | 0
1443 | 24.05 | 5 | 12 | 5 | 12 | 70.0025 | 40 | 9.3899e-07 | 3.5481 | -4.1192e-07 | 1.3063e-05 | 4.8004 | 0 | 4.8004 |  | 15.2004 | 4 | 15.2004 | 70.0025 | 35.0012 | 15 | 35 | 0.0012352 | -0.00039128 | 9.3899e-07 | 2.5745e-07 | 1 | 0
1444 | 24.0667 | 5 | 12 | 5 | 12 | 70.0024 | 40 | 5.311e-07 | 3.5481 | -4.0789e-07 | 7.3884e-06 | 4.8004 | 0 | 4.8004 |  | 15.2004 | 4 | 15.2004 | 70.0024 | 35.0012 | 15 | 35 | 0.0012197 | 0.00082845 | 5.311e-07 | 2.5493e-07 | 1 | 0
1445 | 24.0833 | 5 | 12 | 5 | 12 | 70.0024 | 40 | 1.2776e-07 | 3.5481 | -4.0334e-07 | 1.7774e-06 | 4.8004 | 0 | 4.8004 |  | 15.2004 | 4 | 15.2004 | 70.0024 | 35.0012 | 15 | 35 | 0.0012027 | 0.0020312 | 1.2776e-07 | 2.5208e-07 | 1 | 0
1446 | 24.1 | 5 | 12 | 5 | 12 | 70.0024 | 40 | -2.7051e-07 | 3.5481 | -3.9828e-07 | -3.7633e-06 | 4.8004 | 0 | 4.8004 |  | 15.2004 | 4 | 15.2004 | 70.0024 | 35.0012 | 15 | 35 | 0.0011843 | 0.0032155 | 2.7051e-07 | 2.4892e-07 | 1 | 0
1447 | 24.1167 | 5 | 12 | 5 | 12 | 70.0023 | 40 | -6.6324e-07 | 3.5481 | -3.9273e-07 | -9.2268e-06 | 4.8004 | 0 | 4.8004 |  | 15.2004 | 4 | 15.2004 | 70.0023 | 35.0012 | 15 | 35 | 0.0011644 | 0.0043799 | 6.6324e-07 | 2.4546e-07 | 1 | 0
1448 | 24.1333 | 5 | 12 | 5 | 12 | 70.0023 | 40 | -1.0499e-06 | 3.5481 | -3.867e-07 | -1.4606e-05 | 4.8004 | 0 | 4.8004 |  | 15.2004 | 4 | 15.2004 | 70.0023 | 35.0011 | 15 | 35 | 0.0011431 | 0.005523 | 1.0499e-06 | 2.4169e-07 | 1 | 0
1449 | 24.15 | 5 | 12 | 5 | 12 | 70.0022 | 40 | -1.4302e-06 | 3.5481 | -3.8021e-07 | -1.9896e-05 | 4.8004 | 0 | 4.8004 |  | 15.2004 | 4 | 15.2004 | 70.0022 | 35.0011 | 15 | 35 | 0.0011206 | 0.0066436 | 1.4302e-06 | 2.3763e-07 | 1 | 0
1450 | 24.1667 | 5 | 12 | 5 | 12 | 70.0022 | 40 | -1.8034e-06 | 3.5481 | -3.7327e-07 | -2.5089e-05 | 4.8004 | 0 | 4.8004 |  | 15.2004 | 4 | 15.2004 | 70.0022 | 35.0011 | 15 | 35 | 0.0010967 | 0.0077403 | 1.8034e-06 | 2.333e-07 | 1 | 0
1451 | 24.1833 | 5 | 12 | 5 | 12 | 70.0021 | 40 | -2.1693e-06 | 3.5481 | -3.659e-07 | -3.0179e-05 | 4.8004 | 0 | 4.8003 |  | 15.2003 | 4 | 15.2003 | 70.0021 | 35.0011 | 15 | 35 | 0.0010716 | 0.0088119 | 2.1693e-06 | 2.2869e-07 | 1 | 0
1452 | 24.2 | 5 | 12 | 5 | 12 | 70.0021 | 40 | -2.5274e-06 | 3.5481 | -3.5811e-07 | -3.5161e-05 | 4.8004 | 0 | 4.8003 |  | 15.2003 | 4 | 15.2003 | 70.0021 | 35.001 | 15 | 35 | 0.0010454 | 0.0098573 | 2.5274e-06 | 2.2382e-07 | 1 | 0
1453 | 24.2167 | 5 | 12 | 5 | 12 | 70.002 | 40 | -2.8774e-06 | 3.5481 | -3.4992e-07 | -4.0029e-05 | 4.8004 | 0 | 4.8003 |  | 15.2003 | 4 | 15.2003 | 70.002 | 35.001 | 15 | 35 | 0.001018 | 0.010875 | 2.8774e-06 | 2.187e-07 | 1 | 0
1454 | 24.2333 | 5 | 12 | 5 | 12 | 70.002 | 40 | -3.2187e-06 | 3.5481 | -3.4135e-07 | -4.4777e-05 | 4.8004 | 0 | 4.8003 |  | 15.2003 | 4 | 15.2003 | 70.002 | 35.001 | 15 | 35 | 0.00098956 | 0.011865 | 3.2187e-06 | 2.1334e-07 | 1 | 0
1455 | 24.25 | 5 | 12 | 5 | 12 | 70.0019 | 40 | -3.5511e-06 | 3.5481 | -3.3241e-07 | -4.9402e-05 | 4.8004 | 0 | 4.8003 |  | 15.2003 | 4 | 15.2003 | 70.0019 | 35.001 | 15 | 35 | 0.0009601 | 0.012825 | 3.5511e-06 | 2.0776e-07 | 1 | 0
1456 | 24.2667 | 5 | 12 | 5 | 12 | 70.0019 | 40 | -3.8743e-06 | 3.5481 | -3.2312e-07 | -5.3897e-05 | 4.8004 | 0 | 4.8003 |  | 15.2003 | 4 | 15.2003 | 70.0019 | 35.0009 | 15 | 35 | 0.00092967 | 0.013755 | 3.8743e-06 | 2.0195e-07 | 1 | 0
1457 | 24.2833 | 5 | 12 | 5 | 12 | 70.0018 | 40 | -4.1878e-06 | 3.5481 | -3.135e-07 | -5.8258e-05 | 4.8003 | 0 | 4.8003 |  | 15.2003 | 4 | 15.2003 | 70.0018 | 35.0009 | 15 | 35 | 0.00089833 | 0.014653 | 4.1878e-06 | 1.9594e-07 | 1 | 0
1458 | 24.3 | 5 | 12 | 5 | 12 | 70.0017 | 40 | -4.4913e-06 | 3.5481 | -3.0357e-07 | -6.2481e-05 | 4.8003 | 0 | 4.8003 |  | 15.2003 | 4 | 15.2003 | 70.0017 | 35.0009 | 15 | 35 | 0.00086615 | 0.015519 | 4.4913e-06 | 1.8973e-07 | 1 | 0
1459 | 24.3167 | 5 | 12 | 5 | 12 | 70.0017 | 40 | -4.7847e-06 | 3.5481 | -2.9333e-07 | -6.6562e-05 | 4.8003 | 0 | 4.8003 |  | 15.2003 | 4 | 15.2003 | 70.0017 | 35.0008 | 15 | 35 | 0.00083317 | 0.016352 | 4.7847e-06 | 1.8333e-07 | 1 | 0
1460 | 24.3333 | 5 | 12 | 5 | 12 | 70.0016 | 40 | -5.0675e-06 | 3.5481 | -2.8282e-07 | -7.0496e-05 | 4.8003 | 0 | 4.8003 |  | 15.2003 | 4 | 15.2003 | 70.0016 | 35.0008 | 15 | 35 | 0.00079945 | 0.017152 | 5.0675e-06 | 1.7676e-07 | 1 | 0
1461 | 24.35 | 5 | 12 | 5 | 12 | 70.0015 | 40 | -5.3395e-06 | 3.5481 | -2.7205e-07 | -7.4281e-05 | 4.8003 | 0 | 4.8002 |  | 15.2002 | 4 | 15.2002 | 70.0015 | 35.0008 | 15 | 35 | 0.00076504 | 0.017917 | 5.3395e-06 | 1.7003e-07 | 1 | 0
1462 | 24.3667 | 5 | 12 | 5 | 12 | 70.0015 | 40 | -5.6006e-06 | 3.5481 | -2.6104e-07 | -7.7913e-05 | 4.8003 | 0 | 4.8002 |  | 15.2002 | 4 | 15.2002 | 70.0015 | 35.0007 | 15 | 35 | 0.00073002 | 0.018647 | 5.6006e-06 | 1.6315e-07 | 1 | 0
1463 | 24.3833 | 5 | 12 | 5 | 12 | 70.0014 | 40 | -5.8504e-06 | 3.5481 | -2.4981e-07 | -8.1388e-05 | 4.8003 | 0 | 4.8002 |  | 15.2002 | 4 | 15.2002 | 70.0014 | 35.0007 | 15 | 35 | 0.00069442 | 0.019341 | 5.8504e-06 | 1.5613e-07 | 1 | 0
1464 | 24.4 | 5 | 12 | 5 | 12 | 70.0013 | 40 | -6.0888e-06 | 3.548 | -2.3837e-07 | -8.4704e-05 | 4.8003 | 0 | 4.8002 |  | 15.2002 | 4 | 15.2002 | 70.0013 | 35.0007 | 15 | 35 | 0.00065832 | 0.02 | 6.0888e-06 | 1.4898e-07 | 1 | 0
1465 | 24.4167 | 5 | 12 | 5 | 12 | 70.0012 | 40 | -6.3155e-06 | 3.548 | -2.2675e-07 | -8.7859e-05 | 4.8003 | 0 | 4.8002 |  | 15.2002 | 4 | 15.2002 | 70.0012 | 35.0006 | 15 | 35 | 0.00062176 | 0.020621 | 6.3155e-06 | 1.4172e-07 | 1 | 0
1466 | 24.4333 | 5 | 12 | 5 | 12 | 70.0012 | 40 | -6.5305e-06 | 3.548 | -2.1496e-07 | -9.0849e-05 | 4.8003 | 0 | 4.8002 |  | 15.2002 | 4 | 15.2002 | 70.0012 | 35.0006 | 15 | 35 | 0.0005848 | 0.021206 | 6.5305e-06 | 1.3435e-07 | 1 | 0
1467 | 24.45 | 5 | 12 | 5 | 12 | 70.0011 | 40 | -6.7335e-06 | 3.548 | -2.0302e-07 | -9.3673e-05 | 4.8003 | 0 | 4.8002 |  | 15.2002 | 4 | 15.2002 | 70.0011 | 35.0005 | 15 | 35 | 0.00054751 | 0.021754 | 6.7335e-06 | 1.2689e-07 | 1 | 0
1468 | 24.4667 | 5 | 12 | 5 | 12 | 70.001 | 40 | -6.9244e-06 | 3.548 | -1.9096e-07 | -9.633e-05 | 4.8003 | 0 | 4.8002 |  | 15.2002 | 4 | 15.2002 | 70.001 | 35.0005 | 15 | 35 | 0.00050993 | 0.022264 | 6.9244e-06 | 1.1935e-07 | 1 | 0
1469 | 24.4833 | 5 | 12 | 5 | 12 | 70.0009 | 40 | -7.1032e-06 | 3.548 | -1.7878e-07 | -9.8817e-05 | 4.8002 | 0 | 4.8002 |  | 15.2002 | 4 | 15.2002 | 70.0009 | 35.0005 | 15 | 35 | 0.00047212 | 0.022736 | 7.1032e-06 | 1.1174e-07 | 1 | 0
1470 | 24.5 | 5 | 12 | 5 | 12 | 70.0009 | 40 | -7.2697e-06 | 3.548 | -1.6651e-07 | -0.00010113 | 4.8002 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0009 | 35.0004 | 15 | 35 | 0.00043415 | 0.02317 | 7.2697e-06 | 1.0407e-07 | 1 | 0
1471 | 24.5167 | 5 | 12 | 5 | 12 | 70.0008 | 40 | -7.4239e-06 | 3.548 | -1.5416e-07 | -0.00010328 | 4.8002 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0008 | 35.0004 | 15 | 35 | 0.00039606 | 0.023566 | 7.4239e-06 | 9.6352e-08 | 1 | 0
1472 | 24.5333 | 5 | 12 | 5 | 12 | 70.0007 | 40 | -7.5657e-06 | 3.548 | -1.4176e-07 | -0.00010525 | 4.8002 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0007 | 35.0004 | 15 | 35 | 0.00035791 | 0.023924 | 7.5657e-06 | 8.8602e-08 | 1 | 0
1473 | 24.55 | 5 | 12 | 5 | 12 | 70.0006 | 40 | -7.695e-06 | 3.548 | -1.2933e-07 | -0.00010705 | 4.8002 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0006 | 35.0003 | 15 | 35 | 0.00031975 | 0.024244 | 7.695e-06 | 8.0828e-08 | 1 | 0
1474 | 24.5667 | 5 | 12 | 5 | 12 | 70.0006 | 40 | -7.8118e-06 | 3.548 | -1.1687e-07 | -0.00010867 | 4.8002 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0006 | 35.0003 | 15 | 35 | 0.00028164 | 0.024525 | 7.8118e-06 | 7.3043e-08 | 1 | 0
1475 | 24.5833 | 5 | 12 | 5 | 12 | 70.0005 | 40 | -7.9163e-06 | 3.548 | -1.0441e-07 | -0.00011013 | 4.8002 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0005 | 35.0002 | 15 | 35 | 0.00024364 | 0.024769 | 7.9163e-06 | 6.5256e-08 | 1 | 0
1476 | 24.6 | 5 | 12 | 5 | 12 | 70.0004 | 40 | -8.0082e-06 | 3.548 | -9.1965e-08 | -0.00011141 | 4.8002 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0004 | 35.0002 | 15 | 35 | 0.00020578 | 0.024975 | 8.0082e-06 | 5.7478e-08 | 1 | 0
1477 | 24.6167 | 5 | 12 | 5 | 12 | 70.0003 | 40 | -8.0878e-06 | 3.5479 | -7.9555e-08 | -0.00011251 | 4.8002 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0003 | 35.0002 | 15 | 35 | 0.00016813 | 0.025143 | 8.0878e-06 | 4.9722e-08 | 1 | 0
1478 | 24.6333 | 5 | 12 | 5 | 12 | 70.0003 | 40 | -8.155e-06 | 3.5479 | -6.7193e-08 | -0.00011345 | 4.8002 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0003 | 35.0001 | 15 | 35 | 0.00013073 | 0.025273 | 8.155e-06 | 4.1996e-08 | 1 | 0
1479 | 24.65 | 5 | 12 | 5 | 12 | 70.0002 | 40 | -8.2099e-06 | 3.5479 | -5.4898e-08 | -0.00011421 | 4.8001 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0002 | 35.0001 | 15 | 35 | 9.3629e-05 | 0.025367 | 8.2099e-06 | 3.4311e-08 | 1 | 0
1480 | 24.6667 | 5 | 12 | 5 | 12 | 70.0001 | 40 | -8.2526e-06 | 3.5479 | -4.2686e-08 | -0.00011481 | 4.8001 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35.0001 | 15 | 35 | 5.6882e-05 | 0.025424 | 8.2526e-06 | 2.6679e-08 | 1 | 0
1481 | 24.6833 | 5 | 12 | 5 | 12 | 70 | 40 | -8.2831e-06 | 3.5479 | -3.0573e-08 | -0.00011523 | 4.8001 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | 2.0532e-05 | 0.025444 | 8.2831e-06 | 1.9108e-08 | 1 | 0
1482 | 24.7 | 5 | 12 | 5 | 12 | 70 | 40 | -8.3017e-06 | 3.5479 | -1.8574e-08 | -0.00011549 | 4.8001 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -1.5374e-05 | 0.025429 | 8.3017e-06 | 1.1609e-08 | 1 | 0
1483 | 24.7167 | 5 | 12 | 5 | 12 | 69.9999 | 40 | -8.3084e-06 | 3.5479 | -6.7044e-09 | -0.00011558 | 4.8001 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 34.9999 | 15 | 35 | -5.0793e-05 | 0.025378 | 8.3084e-06 | 4.1902e-09 | 1 | 0
1484 | 24.7333 | 5 | 12 | 5 | 12 | 69.9998 | 40 | -8.3034e-06 | 3.5479 | 5.0202e-09 | -0.00011551 | 4.8001 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9998 | 34.9999 | 15 | 35 | -8.5681e-05 | 0.025293 | 8.3034e-06 | -3.1376e-09 | -1 | -2
1485 | 24.75 | 5 | 12 | 5 | 12 | 69.9998 | 40 | -8.2868e-06 | 3.5479 | 1.6586e-08 | -0.00011528 | 4.8001 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9998 | 34.9999 | 15 | 35 | -0.00012 | 0.025173 | 8.2868e-06 | -1.0366e-08 | -1 | 0
1486 | 24.7667 | 5 | 12 | 5 | 12 | 69.9997 | 40 | -8.2588e-06 | 3.5479 | 2.7978e-08 | -0.00011489 | 4.8001 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9997 | 34.9998 | 15 | 35 | -0.0001537 | 0.025019 | 8.2588e-06 | -1.7486e-08 | -1 | 0
1487 | 24.7833 | 5 | 12 | 5 | 12 | 69.9996 | 40 | -8.2196e-06 | 3.5479 | 3.9183e-08 | -0.00011435 | 4.8001 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9996 | 34.9998 | 15 | 35 | -0.00018675 | 0.024832 | 8.2196e-06 | -2.4489e-08 | -1 | 0
1488 | 24.8 | 5 | 12 | 5 | 12 | 69.9996 | 40 | -8.1695e-06 | 3.5479 | 5.0187e-08 | -0.00011365 | 4.8 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9996 | 34.9998 | 15 | 35 | -0.0002191 | 0.024613 | 8.1695e-06 | -3.1367e-08 | -1 | 0
1489 | 24.8167 | 5 | 12 | 5 | 12 | 69.9995 | 40 | -8.1085e-06 | 3.5479 | 6.0979e-08 | -0.0001128 | 4.8 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9995 | 34.9997 | 15 | 35 | -0.00025074 | 0.024362 | 8.1085e-06 | -3.8112e-08 | -1 | 0
1490 | 24.8333 | 5 | 12 | 5 | 12 | 69.9994 | 40 | -8.0369e-06 | 3.5478 | 7.1544e-08 | -0.00011181 | 4.8 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9994 | 34.9997 | 15 | 35 | -0.00028161 | 0.024081 | 8.0369e-06 | -4.4715e-08 | -1 | 0
1491 | 24.85 | 5 | 12 | 5 | 12 | 69.9994 | 40 | -7.9551e-06 | 3.5478 | 8.1873e-08 | -0.00011067 | 4.8 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9994 | 34.9997 | 15 | 35 | -0.00031168 | 0.023769 | 7.9551e-06 | -5.1171e-08 | -1 | 0
1492 | 24.8667 | 5 | 12 | 5 | 12 | 69.9993 | 40 | -7.8631e-06 | 3.5478 | 9.1953e-08 | -0.00010939 | 4.8 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9993 | 34.9997 | 15 | 35 | -0.00034093 | 0.023428 | 7.8631e-06 | -5.747e-08 | -1 | 0
1493 | 24.8833 | 5 | 12 | 5 | 12 | 69.9993 | 40 | -7.7613e-06 | 3.5478 | 1.0177e-07 | -0.00010797 | 4.8 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9993 | 34.9996 | 15 | 35 | -0.00036932 | 0.023059 | 7.7613e-06 | -6.3608e-08 | -1 | 0
1494 | 24.9 | 5 | 12 | 5 | 12 | 69.9992 | 40 | -7.65e-06 | 3.5478 | 1.1132e-07 | -0.00010642 | 4.8 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9992 | 34.9996 | 15 | 35 | -0.00039682 | 0.022662 | 7.65e-06 | -6.9577e-08 | -1 | 0
1495 | 24.9167 | 5 | 12 | 5 | 12 | 69.9992 | 40 | -7.5294e-06 | 3.5478 | 1.2059e-07 | -0.00010475 | 4.8 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9992 | 34.9996 | 15 | 35 | -0.00042341 | 0.022239 | 7.5294e-06 | -7.5371e-08 | -1 | 0
1496 | 24.9333 | 5 | 12 | 5 | 12 | 69.9991 | 40 | -7.3998e-06 | 3.5478 | 1.2957e-07 | -0.00010294 | 4.8 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9991 | 34.9996 | 15 | 35 | -0.00044907 | 0.02179 | 7.3998e-06 | -8.0984e-08 | -1 | 0
1497 | 24.95 | 5 | 12 | 5 | 12 | 69.9991 | 40 | -7.2616e-06 | 3.5478 | 1.3826e-07 | -0.00010102 | 4.7999 | 0 | 4.7998 |  | 15.1998 | 4 | 15.1998 | 69.9991 | 34.9995 | 15 | 35 | -0.00047376 | 0.021316 | 7.2616e-06 | -8.6411e-08 | -1 | 0
1498 | 24.9667 | 5 | 12 | 5 | 12 | 69.999 | 40 | -7.1149e-06 | 3.5478 | 1.4663e-07 | -9.898e-05 | 4.7999 | 0 | 4.7998 |  | 15.1998 | 4 | 15.1998 | 69.999 | 34.9995 | 15 | 35 | -0.00049746 | 0.020818 | 7.1149e-06 | -9.1646e-08 | -1 | 0
1499 | 24.9833 | 5 | 12 | 5 | 12 | 69.999 | 40 | -6.9603e-06 | 3.5478 | 1.547e-07 | -9.6828e-05 | 4.7999 | 0 | 4.7998 |  | 15.1998 | 4 | 15.1998 | 69.999 | 34.9995 | 15 | 35 | -0.00052017 | 0.020298 | 6.9603e-06 | -9.6685e-08 | -1 | 0
1500 | 25 | 5 | 12 | 5 | 12 | 69.9989 | 40 | -6.7978e-06 | 3.5478 | 1.6244e-07 | -9.4568e-05 | 4.7999 | 0 | 4.7998 |  | 15.1998 | 4 | 15.1998 | 69.9989 | 34.9995 | 15 | 35 | -0.00054184 | 0.019756 | 6.7978e-06 | -1.0152e-07 | -1 | 0
1501 | 25.0167 | 5 | 12 | 5 | 12 | 69.9989 | 40 | -6.628e-06 | 3.5478 | 1.6985e-07 | -9.2205e-05 | 4.7999 | 0 | 4.7998 |  | 15.1998 | 4 | 15.1998 | 69.9989 | 34.9994 | 15 | 35 | -0.00056248 | 0.019194 | 6.628e-06 | -1.0616e-07 | -1 | 0
1502 | 25.0333 | 5 | 12 | 5 | 12 | 69.9988 | 40 | -6.451e-06 | 3.5478 | 1.7693e-07 | -8.9744e-05 | 4.7999 | 0 | 4.7998 |  | 15.1998 | 4 | 15.1998 | 69.9988 | 34.9994 | 15 | 35 | -0.00058207 | 0.018612 | 6.451e-06 | -1.1058e-07 | -1 | 0
1503 | 25.05 | 5 | 12 | 5 | 12 | 69.9988 | 40 | -6.2674e-06 | 3.5477 | 1.8367e-07 | -8.7189e-05 | 4.7999 | 0 | 4.7998 |  | 15.1998 | 4 | 15.1998 | 69.9988 | 34.9994 | 15 | 35 | -0.00060058 | 0.018011 | 6.2674e-06 | -1.1479e-07 | -1 | 0
1504 | 25.0667 | 5 | 12 | 5 | 12 | 69.9988 | 40 | -6.0773e-06 | 3.5477 | 1.9006e-07 | -8.4545e-05 | 4.7999 | 0 | 4.7998 |  | 15.1998 | 4 | 15.1998 | 69.9988 | 34.9994 | 15 | 35 | -0.00061801 | 0.017393 | 6.0773e-06 | -1.1879e-07 | -1 | 0
1505 | 25.0833 | 5 | 12 | 5 | 12 | 69.9987 | 40 | -5.8812e-06 | 3.5477 | 1.9611e-07 | -8.1817e-05 | 4.7999 | 0 | 4.7998 |  | 15.1998 | 4 | 15.1998 | 69.9987 | 34.9994 | 15 | 35 | -0.00063435 | 0.016759 | 5.8812e-06 | -1.2257e-07 | -1 | 0
1506 | 25.1 | 5 | 12 | 5 | 12 | 69.9987 | 40 | -5.6794e-06 | 3.5477 | 2.018e-07 | -7.9009e-05 | 4.7999 | 0 | 4.7998 |  | 15.1998 | 4 | 15.1998 | 69.9987 | 34.9994 | 15 | 35 | -0.00064959 | 0.016109 | 5.6794e-06 | -1.2612e-07 | -1 | 0
1507 | 25.1167 | 5 | 12 | 5 | 12 | 69.9987 | 40 | -5.4723e-06 | 3.5477 | 2.0714e-07 | -7.6128e-05 | 4.7999 | 0 | 4.7998 |  | 15.1998 | 4 | 15.1998 | 69.9987 | 34.9993 | 15 | 35 | -0.00066372 | 0.015445 | 5.4723e-06 | -1.2946e-07 | -1 | 0
1508 | 25.1333 | 5 | 12 | 5 | 12 | 69.9986 | 40 | -5.2602e-06 | 3.5477 | 2.1211e-07 | -7.3177e-05 | 4.7999 | 0 | 4.7998 |  | 15.1998 | 4 | 15.1998 | 69.9986 | 34.9993 | 15 | 35 | -0.00067674 | 0.014769 | 5.2602e-06 | -1.3257e-07 | -1 | 0
1509 | 25.15 | 5 | 12 | 5 | 12 | 69.9986 | 40 | -5.0434e-06 | 3.5477 | 2.1673e-07 | -7.0162e-05 | 4.7998 | 0 | 4.7998 |  | 15.1998 | 4 | 15.1998 | 69.9986 | 34.9993 | 15 | 35 | -0.00068864 | 0.01408 | 5.0434e-06 | -1.3545e-07 | -1 | 0
1510 | 25.1667 | 5 | 12 | 5 | 12 | 69.9986 | 40 | -4.8225e-06 | 3.5477 | 2.2098e-07 | -6.7088e-05 | 4.7998 | 0 | 4.7998 |  | 15.1998 | 4 | 15.1998 | 69.9986 | 34.9993 | 15 | 35 | -0.00069942 | 0.013381 | 4.8225e-06 | -1.3811e-07 | -1 | 0
1511 | 25.1833 | 5 | 12 | 5 | 12 | 69.9986 | 40 | -4.5976e-06 | 3.5477 | 2.2486e-07 | -6.396e-05 | 4.7998 | 0 | 4.7998 |  | 15.1998 | 4 | 15.1998 | 69.9986 | 34.9993 | 15 | 35 | -0.00070909 | 0.012672 | 4.5976e-06 | -1.4054e-07 | -1 | 0
1512 | 25.2 | 5 | 12 | 5 | 12 | 69.9986 | 40 | -4.3692e-06 | 3.5477 | 2.2838e-07 | -6.0782e-05 | 4.7998 | 0 | 4.7998 |  | 15.1998 | 4 | 15.1998 | 69.9986 | 34.9993 | 15 | 35 | -0.00071763 | 0.011954 | 4.3692e-06 | -1.4274e-07 | -1 | 0
1513 | 25.2167 | 5 | 12 | 5 | 12 | 69.9985 | 40 | -4.1377e-06 | 3.5477 | 2.3154e-07 | -5.7561e-05 | 4.7998 | 0 | 4.7998 |  | 15.1998 | 4 | 15.1998 | 69.9985 | 34.9993 | 15 | 35 | -0.00072506 | 0.011229 | 4.1377e-06 | -1.4471e-07 | -1 | 0
1514 | 25.2333 | 5 | 12 | 5 | 12 | 69.9985 | 40 | -3.9033e-06 | 3.5477 | 2.3433e-07 | -5.4302e-05 | 4.7998 | 0 | 4.7998 |  | 15.1998 | 4 | 15.1998 | 69.9985 | 34.9993 | 15 | 35 | -0.00073137 | 0.010498 | 3.9033e-06 | -1.4646e-07 | -1 | 0
1515 | 25.25 | 5 | 12 | 5 | 12 | 69.9985 | 40 | -3.6666e-06 | 3.5477 | 2.3675e-07 | -5.1008e-05 | 4.7998 | 0 | 4.7998 |  | 15.1998 | 4 | 15.1998 | 69.9985 | 34.9993 | 15 | 35 | -0.00073658 | 0.009761 | 3.6666e-06 | -1.4797e-07 | -1 | 0
1516 | 25.2667 | 5 | 12 | 5 | 12 | 69.9985 | 40 | -3.4278e-06 | 3.5477 | 2.3882e-07 | -4.7686e-05 | 4.7998 | 0 | 4.7998 |  | 15.1998 | 4 | 15.1998 | 69.9985 | 34.9993 | 15 | 35 | -0.00074069 | 0.0090203 | 3.4278e-06 | -1.4926e-07 | -1 | 0
1517 | 25.2833 | 5 | 12 | 5 | 12 | 69.9985 | 40 | -3.1873e-06 | 3.5477 | 2.4052e-07 | -4.434e-05 | 4.7998 | 0 | 4.7998 |  | 15.1998 | 4 | 15.1998 | 69.9985 | 34.9993 | 15 | 35 | -0.00074371 | 0.0082765 | 3.1873e-06 | -1.5032e-07 | -1 | 0
1518 | 25.3 | 5 | 12 | 5 | 12 | 69.9985 | 40 | -2.9454e-06 | 3.5477 | 2.4186e-07 | -4.0975e-05 | 4.7998 | 0 | 4.7998 |  | 15.1998 | 4 | 15.1998 | 69.9985 | 34.9993 | 15 | 35 | -0.00074565 | 0.0075309 | 2.9454e-06 | -1.5116e-07 | -1 | 0
1519 | 25.3167 | 5 | 12 | 5 | 12 | 69.9985 | 40 | -2.7025e-06 | 3.5477 | 2.4285e-07 | -3.7597e-05 | 4.7998 | 0 | 4.7998 |  | 15.1998 | 4 | 15.1998 | 69.9985 | 34.9993 | 15 | 35 | -0.00074652 | 0.0067844 | 2.7025e-06 | -1.5178e-07 | -1 | 0
1520 | 25.3333 | 5 | 12 | 5 | 12 | 69.9985 | 40 | -2.4591e-06 | 3.5477 | 2.4348e-07 | -3.4209e-05 | 4.7998 | 0 | 4.7998 |  | 15.1998 | 4 | 15.1998 | 69.9985 | 34.9993 | 15 | 35 | -0.00074633 | 0.006038 | 2.4591e-06 | -1.5217e-07 | -1 | 0
1521 | 25.35 | 5 | 12 | 5 | 12 | 69.9985 | 40 | -2.2153e-06 | 3.5477 | 2.4376e-07 | -3.0818e-05 | 4.7998 | 0 | 4.7998 |  | 15.1998 | 4 | 15.1998 | 69.9985 | 34.9993 | 15 | 35 | -0.0007451 | 0.0052929 | 2.2153e-06 | -1.5235e-07 | -1 | 0
1522 | 25.3667 | 5 | 12 | 5 | 12 | 69.9985 | 40 | -1.9716e-06 | 3.5477 | 2.437e-07 | -2.7428e-05 | 4.7998 | 0 | 4.7998 |  | 15.1998 | 4 | 15.1998 | 69.9985 | 34.9993 | 15 | 35 | -0.00074284 | 0.0045501 | 1.9716e-06 | -1.5231e-07 | -1 | 0
1523 | 25.3833 | 5 | 12 | 5 | 12 | 69.9985 | 40 | -1.7283e-06 | 3.5477 | 2.433e-07 | -2.4043e-05 | 4.7998 | 0 | 4.7998 |  | 15.1998 | 4 | 15.1998 | 69.9985 | 34.9993 | 15 | 35 | -0.00073957 | 0.0038105 | 1.7283e-06 | -1.5206e-07 | -1 | 0
1524 | 25.4 | 5 | 12 | 5 | 12 | 69.9985 | 40 | -1.4857e-06 | 3.5477 | 2.4256e-07 | -2.0669e-05 | 4.7998 | 0 | 4.7998 |  | 15.1998 | 4 | 15.1998 | 69.9985 | 34.9993 | 15 | 35 | -0.00073531 | 0.0030752 | 1.4857e-06 | -1.516e-07 | -1 | 0
1525 | 25.4167 | 5 | 12 | 5 | 12 | 69.9985 | 40 | -1.2443e-06 | 3.5477 | 2.4149e-07 | -1.7309e-05 | 4.7998 | 0 | 4.7998 |  | 15.1998 | 4 | 15.1998 | 69.9985 | 34.9993 | 15 | 35 | -0.00073007 | 0.0023451 | 1.2443e-06 | -1.5093e-07 | -1 | 0
1526 | 25.4333 | 5 | 12 | 5 | 12 | 69.9986 | 40 | -1.0042e-06 | 3.5477 | 2.401e-07 | -1.3969e-05 | 4.7998 | 0 | 4.7998 |  | 15.1998 | 4 | 15.1998 | 69.9986 | 34.9993 | 15 | 35 | -0.00072388 | 0.0016213 | 1.0042e-06 | -1.5006e-07 | -1 | 0
1527 | 25.45 | 5 | 12 | 5 | 12 | 69.9986 | 40 | -7.6576e-07 | 3.5477 | 2.3839e-07 | -1.0653e-05 | 4.7998 | 0 | 4.7998 |  | 15.1998 | 4 | 15.1998 | 69.9986 | 34.9993 | 15 | 35 | -0.00071675 | 0.00090451 | 7.6576e-07 | -1.4899e-07 | -1 | 0
1528 | 25.4667 | 5 | 12 | 5 | 12 | 69.9986 | 40 | -5.2939e-07 | 3.5477 | 2.3637e-07 | -7.3646e-06 | 4.7998 | 0 | 4.7998 |  | 15.1998 | 4 | 15.1998 | 69.9986 | 34.9993 | 15 | 35 | -0.00070872 | 0.00019579 | 5.2939e-07 | -1.4773e-07 | -1 | 0
1529 | 25.4833 | 5 | 12 | 5 | 12 | 69.9986 | 40 | -2.9535e-07 | 3.5477 | 2.3404e-07 | -4.1088e-06 | 4.7998 | 0 | 4.7998 |  | 15.1998 | 4 | 15.1998 | 69.9986 | 34.9993 | 15 | 35 | -0.00069979 | -0.000504 | 2.9535e-07 | -1.4628e-07 | -1 | 0
1530 | 25.5 | 5 | 12 | 5 | 12 | 69.9986 | 40 | -6.3931e-08 | 3.5477 | 2.3142e-07 | -8.8938e-07 | 4.7998 | 0 | 4.7998 |  | 15.1998 | 4 | 15.1998 | 69.9986 | 34.9993 | 15 | 35 | -0.00069 | -0.001194 | 6.3931e-08 | -1.4464e-07 | -1 | 0
1531 | 25.5167 | 5 | 12 | 5 | 12 | 69.9986 | 40 | 1.6457e-07 | 3.5477 | 2.285e-07 | 2.2894e-06 | 4.7998 | 0 | 4.7998 |  | 15.1998 | 4 | 15.1998 | 69.9986 | 34.9993 | 15 | 35 | -0.00067937 | -0.0018734 | 1.6457e-07 | -1.4281e-07 | -1 | 0
1532 | 25.5333 | 5 | 12 | 5 | 12 | 69.9987 | 40 | 3.8988e-07 | 3.5477 | 2.2531e-07 | 5.4238e-06 | 4.7998 | 0 | 4.7998 |  | 15.1998 | 4 | 15.1998 | 69.9987 | 34.9993 | 15 | 35 | -0.00066793 | -0.0025413 | 3.8988e-07 | -1.4082e-07 | -1 | 0
1533 | 25.55 | 5 | 12 | 5 | 12 | 69.9987 | 40 | 6.1171e-07 | 3.5477 | 2.2184e-07 | 8.5099e-06 | 4.7998 | 0 | 4.7998 |  | 15.1998 | 4 | 15.1998 | 69.9987 | 34.9993 | 15 | 35 | -0.0006557 | -0.003197 | 6.1171e-07 | -1.3865e-07 | -1 | 0
1534 | 25.5667 | 5 | 12 | 5 | 12 | 69.9987 | 40 | 8.2981e-07 | 3.5477 | 2.181e-07 | 1.1544e-05 | 4.7998 | 0 | 4.7998 |  | 15.1998 | 4 | 15.1998 | 69.9987 | 34.9994 | 15 | 35 | -0.00064271 | -0.0038397 | 8.2981e-07 | -1.3631e-07 | -1 | 0
1535 | 25.5833 | 5 | 12 | 5 | 12 | 69.9987 | 40 | 1.0439e-06 | 3.5477 | 2.1411e-07 | 1.4523e-05 | 4.7998 | 0 | 4.7998 |  | 15.1998 | 4 | 15.1998 | 69.9987 | 34.9994 | 15 | 35 | -0.00062899 | -0.0044687 | 1.0439e-06 | -1.3382e-07 | -1 | 0
1536 | 25.6 | 5 | 12 | 5 | 12 | 69.9988 | 40 | 1.2538e-06 | 3.5477 | 2.0986e-07 | 1.7442e-05 | 4.7998 | 0 | 4.7998 |  | 15.1998 | 4 | 15.1998 | 69.9988 | 34.9994 | 15 | 35 | -0.00061456 | -0.0050832 | 1.2538e-06 | -1.3116e-07 | -1 | 0
1537 | 25.6167 | 5 | 12 | 5 | 12 | 69.9988 | 40 | 1.4592e-06 | 3.5477 | 2.0538e-07 | 2.0299e-05 | 4.7998 | 0 | 4.7998 |  | 15.1998 | 4 | 15.1998 | 69.9988 | 34.9994 | 15 | 35 | -0.00059946 | -0.0056827 | 1.4592e-06 | -1.2836e-07 | -1 | 0
1538 | 25.6333 | 5 | 12 | 5 | 12 | 69.9988 | 40 | 1.6598e-06 | 3.5477 | 2.0067e-07 | 2.3091e-05 | 4.7998 | 0 | 4.7998 |  | 15.1998 | 4 | 15.1998 | 69.9988 | 34.9994 | 15 | 35 | -0.00058372 | -0.0062664 | 1.6598e-06 | -1.2542e-07 | -1 | 0
1539 | 25.65 | 5 | 12 | 5 | 12 | 69.9989 | 40 | 1.8556e-06 | 3.5477 | 1.9574e-07 | 2.5814e-05 | 4.7998 | 0 | 4.7998 |  | 15.1998 | 4 | 15.1998 | 69.9989 | 34.9994 | 15 | 35 | -0.00056737 | -0.0068338 | 1.8556e-06 | -1.2234e-07 | -1 | 0
1540 | 25.6667 | 5 | 12 | 5 | 12 | 69.9989 | 40 | 2.0462e-06 | 3.5477 | 1.906e-07 | 2.8466e-05 | 4.7998 | 0 | 4.7998 |  | 15.1998 | 4 | 15.1998 | 69.9989 | 34.9994 | 15 | 35 | -0.00055043 | -0.0073842 | 2.0462e-06 | -1.1913e-07 | -1 | 0
1541 | 25.6833 | 5 | 12 | 5 | 12 | 69.9989 | 40 | 2.2314e-06 | 3.5477 | 1.8526e-07 | 3.1043e-05 | 4.7998 | 0 | 4.7998 |  | 15.1998 | 4 | 15.1998 | 69.9989 | 34.9995 | 15 | 35 | -0.00053294 | -0.0079172 | 2.2314e-06 | -1.1579e-07 | -1 | 0
1542 | 25.7 | 5 | 12 | 5 | 12 | 69.999 | 40 | 2.4112e-06 | 3.5477 | 1.7973e-07 | 3.3543e-05 | 4.7998 | 0 | 4.7998 |  | 15.1998 | 4 | 15.1998 | 69.999 | 34.9995 | 15 | 35 | -0.00051493 | -0.0084321 | 2.4112e-06 | -1.1233e-07 | -1 | 0
1543 | 25.7167 | 5 | 12 | 5 | 12 | 69.999 | 40 | 2.5852e-06 | 3.5477 | 1.7402e-07 | 3.5964e-05 | 4.7998 | 0 | 4.7998 |  | 15.1998 | 4 | 15.1998 | 69.999 | 34.9995 | 15 | 35 | -0.00049644 | -0.0089285 | 2.5852e-06 | -1.0876e-07 | -1 | 0
1544 | 25.7333 | 5 | 12 | 5 | 12 | 69.999 | 40 | 2.7533e-06 | 3.5477 | 1.6814e-07 | 3.8303e-05 | 4.7998 | 0 | 4.7998 |  | 15.1998 | 4 | 15.1998 | 69.999 | 34.9995 | 15 | 35 | -0.00047749 | -0.009406 | 2.7533e-06 | -1.0509e-07 | -1 | 0
1545 | 25.75 | 5 | 12 | 5 | 12 | 69.9991 | 40 | 2.9154e-06 | 3.5477 | 1.621e-07 | 4.0558e-05 | 4.7998 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9991 | 34.9995 | 15 | 35 | -0.00045811 | -0.0098641 | 2.9154e-06 | -1.0131e-07 | -1 | 0
1546 | 25.7667 | 5 | 12 | 5 | 12 | 69.9991 | 40 | 3.0714e-06 | 3.5477 | 1.5591e-07 | 4.2727e-05 | 4.7998 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9991 | 34.9996 | 15 | 35 | -0.00043835 | -0.010302 | 3.0714e-06 | -9.7446e-08 | -1 | 0
1547 | 25.7833 | 5 | 12 | 5 | 12 | 69.9992 | 40 | 3.2209e-06 | 3.5477 | 1.4959e-07 | 4.4808e-05 | 4.7998 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9992 | 34.9996 | 15 | 35 | -0.00041823 | -0.010721 | 3.2209e-06 | -9.3492e-08 | -1 | 0
1548 | 25.8 | 5 | 12 | 5 | 12 | 69.9992 | 40 | 3.3641e-06 | 3.5477 | 1.4313e-07 | 4.68e-05 | 4.7998 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9992 | 34.9996 | 15 | 35 | -0.00039778 | -0.011118 | 3.3641e-06 | -8.9459e-08 | -1 | 0
1549 | 25.8167 | 5 | 12 | 5 | 12 | 69.9992 | 40 | 3.5006e-06 | 3.5477 | 1.3656e-07 | 4.8699e-05 | 4.7998 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9992 | 34.9996 | 15 | 35 | -0.00037705 | -0.011496 | 3.5006e-06 | -8.5353e-08 | -1 | 0
1550 | 25.8333 | 5 | 12 | 5 | 12 | 69.9993 | 40 | 3.6305e-06 | 3.5477 | 1.2989e-07 | 5.0506e-05 | 4.7998 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9993 | 34.9996 | 15 | 35 | -0.00035605 | -0.011852 | 3.6305e-06 | -8.118e-08 | -1 | 0
1551 | 25.85 | 5 | 12 | 5 | 12 | 69.9993 | 40 | 3.7536e-06 | 3.5477 | 1.2312e-07 | 5.2219e-05 | 4.7998 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9993 | 34.9997 | 15 | 35 | -0.00033483 | -0.012186 | 3.7536e-06 | -7.6948e-08 | -1 | 0
1552 | 25.8667 | 5 | 12 | 5 | 12 | 69.9994 | 40 | 3.8699e-06 | 3.5477 | 1.1626e-07 | 5.3836e-05 | 4.7998 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9994 | 34.9997 | 15 | 35 | -0.00031341 | -0.0125 | 3.8699e-06 | -7.2663e-08 | -1 | 0
1553 | 25.8833 | 5 | 12 | 5 | 12 | 69.9994 | 40 | 3.9792e-06 | 3.5477 | 1.0933e-07 | 5.5357e-05 | 4.7999 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9994 | 34.9997 | 15 | 35 | -0.00029183 | -0.012792 | 3.9792e-06 | -6.8332e-08 | -1 | 0
1554 | 25.9 | 5 | 12 | 5 | 12 | 69.9995 | 40 | 4.0816e-06 | 3.5477 | 1.0234e-07 | 5.6781e-05 | 4.7999 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9995 | 34.9997 | 15 | 35 | -0.00027013 | -0.013062 | 4.0816e-06 | -6.3961e-08 | -1 | 0
1555 | 25.9167 | 5 | 12 | 5 | 12 | 69.9995 | 40 | 4.1769e-06 | 3.5477 | 9.5292e-08 | 5.8107e-05 | 4.7999 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9995 | 34.9998 | 15 | 35 | -0.00024833 | -0.01331 | 4.1769e-06 | -5.9558e-08 | -1 | 0
1556 | 25.9333 | 5 | 12 | 5 | 12 | 69.9995 | 40 | 4.2651e-06 | 3.5477 | 8.8205e-08 | 5.9334e-05 | 4.7999 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9995 | 34.9998 | 15 | 35 | -0.00022646 | -0.013537 | 4.2651e-06 | -5.5128e-08 | -1 | 0
1557 | 25.95 | 5 | 12 | 5 | 12 | 69.9996 | 40 | 4.3462e-06 | 3.5477 | 8.1086e-08 | 6.0462e-05 | 4.7999 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9996 | 34.9998 | 15 | 35 | -0.00020456 | -0.013741 | 4.3462e-06 | -5.0679e-08 | -1 | 0
1558 | 25.9667 | 5 | 12 | 5 | 12 | 69.9996 | 40 | 4.4201e-06 | 3.5477 | 7.3946e-08 | 6.1491e-05 | 4.7999 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9996 | 34.9998 | 15 | 35 | -0.00018266 | -0.013924 | 4.4201e-06 | -4.6216e-08 | -1 | 0
1559 | 25.9833 | 5 | 12 | 5 | 12 | 69.9997 | 40 | 4.4869e-06 | 3.5477 | 6.6794e-08 | 6.242e-05 | 4.7999 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9997 | 34.9998 | 15 | 35 | -0.00016078 | -0.014085 | 4.4869e-06 | -4.1746e-08 | -1 | 0
1560 | 26 | 5 | 12 | 5 | 12 | 69.9997 | 40 | 4.5465e-06 | 3.5477 | 5.9643e-08 | 6.3249e-05 | 4.7999 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9997 | 34.9999 | 15 | 35 | -0.00013897 | -0.014224 | 4.5465e-06 | -3.7277e-08 | -1 | 0
1561 | 26.0167 | 5 | 12 | 5 | 12 | 69.9998 | 40 | 4.599e-06 | 3.5478 | 5.25e-08 | 6.398e-05 | 4.7999 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9998 | 34.9999 | 15 | 35 | -0.00011724 | -0.014341 | 4.599e-06 | -3.2812e-08 | -1 | 0
1562 | 26.0333 | 5 | 12 | 5 | 12 | 69.9998 | 40 | 4.6444e-06 | 3.5478 | 4.5377e-08 | 6.4611e-05 | 4.7999 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9998 | 34.9999 | 15 | 35 | -9.563e-05 | -0.014436 | 4.6444e-06 | -2.836e-08 | -1 | 0
1563 | 26.05 | 5 | 12 | 5 | 12 | 69.9999 | 40 | 4.6827e-06 | 3.5478 | 3.8282e-08 | 6.5144e-05 | 4.7999 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 34.9999 | 15 | 35 | -7.4167e-05 | -0.014511 | 4.6827e-06 | -2.3926e-08 | -1 | 0
1564 | 26.0667 | 5 | 12 | 5 | 12 | 69.9999 | 40 | 4.7139e-06 | 3.5478 | 3.1226e-08 | 6.5578e-05 | 4.7999 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 34.9999 | 15 | 35 | -5.288e-05 | -0.014563 | 4.7139e-06 | -1.9516e-08 | -1 | 0
1565 | 26.0833 | 5 | 12 | 5 | 12 | 69.9999 | 40 | 4.7381e-06 | 3.5478 | 2.4218e-08 | 6.5915e-05 | 4.7999 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 35 | 15 | 35 | -3.1794e-05 | -0.014595 | 4.7381e-06 | -1.5136e-08 | -1 | 0
1566 | 26.1 | 5 | 12 | 5 | 12 | 70 | 40 | 4.7554e-06 | 3.5478 | 1.7267e-08 | 6.6155e-05 | 4.7999 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -1.0938e-05 | -0.014606 | 4.7554e-06 | -1.0792e-08 | -1 | 0
1567 | 26.1167 | 5 | 12 | 5 | 12 | 70 | 40 | 4.7658e-06 | 3.5478 | 1.0382e-08 | 6.63e-05 | 4.7999 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | 9.6628e-06 | -0.014597 | 4.7658e-06 | -6.4886e-09 | -1 | 0
1568 | 26.1333 | 5 | 12 | 5 | 12 | 70.0001 | 40 | 4.7694e-06 | 3.5478 | 3.5716e-09 | 6.6349e-05 | 4.7999 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 2.9983e-05 | -0.014567 | 4.7694e-06 | -2.2322e-09 | -1 | 0
1569 | 26.15 | 5 | 12 | 5 | 12 | 70.0001 | 40 | 4.7662e-06 | 3.5478 | -3.1552e-09 | 6.6305e-05 | 4.7999 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 4.9997e-05 | -0.014517 | 4.7662e-06 | 1.972e-09 | 1 | 2
1570 | 26.1667 | 5 | 12 | 5 | 12 | 70.0001 | 40 | 4.7564e-06 | 3.5478 | -9.7903e-09 | 6.6169e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35.0001 | 15 | 35 | 6.9681e-05 | -0.014447 | 4.7564e-06 | 6.1189e-09 | 1 | 0
1571 | 26.1833 | 5 | 12 | 5 | 12 | 70.0002 | 40 | 4.7401e-06 | 3.5478 | -1.6325e-08 | 6.5942e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0002 | 35.0001 | 15 | 35 | 8.9012e-05 | -0.014358 | 4.7401e-06 | 1.0203e-08 | 1 | 0
1572 | 26.2 | 5 | 12 | 5 | 12 | 70.0002 | 40 | 4.7173e-06 | 3.5478 | -2.2753e-08 | 6.5626e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0002 | 35.0001 | 15 | 35 | 0.00010797 | -0.01425 | 4.7173e-06 | 1.4221e-08 | 1 | 0
1573 | 26.2167 | 5 | 12 | 5 | 12 | 70.0003 | 40 | 4.6883e-06 | 3.5478 | -2.9065e-08 | 6.5221e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0003 | 35.0001 | 15 | 35 | 0.00012653 | -0.014123 | 4.6883e-06 | 1.8166e-08 | 1 | 0
1574 | 26.2333 | 5 | 12 | 5 | 12 | 70.0003 | 40 | 4.653e-06 | 3.5478 | -3.5255e-08 | 6.4731e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0003 | 35.0001 | 15 | 35 | 0.00014467 | -0.013979 | 4.653e-06 | 2.2034e-08 | 1 | 0
1575 | 26.25 | 5 | 12 | 5 | 12 | 70.0003 | 40 | 4.6117e-06 | 3.5478 | -4.1315e-08 | 6.4156e-05 | 4.8 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0003 | 35.0002 | 15 | 35 | 0.00016237 | -0.013816 | 4.6117e-06 | 2.5822e-08 | 1 | 0
1576 | 26.2667 | 5 | 12 | 5 | 12 | 70.0004 | 40 | 4.5645e-06 | 3.5478 | -4.7238e-08 | 6.3499e-05 | 4.8 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0004 | 35.0002 | 15 | 35 | 0.00017961 | -0.013637 | 4.5645e-06 | 2.9524e-08 | 1 | 0
1577 | 26.2833 | 5 | 12 | 5 | 12 | 70.0004 | 40 | 4.5114e-06 | 3.5478 | -5.3018e-08 | 6.2761e-05 | 4.8 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0004 | 35.0002 | 15 | 35 | 0.00019638 | -0.01344 | 4.5114e-06 | 3.3136e-08 | 1 | 0
1578 | 26.3 | 5 | 12 | 5 | 12 | 70.0004 | 40 | 4.4528e-06 | 3.5478 | -5.8649e-08 | 6.1945e-05 | 4.8 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0004 | 35.0002 | 15 | 35 | 0.00021266 | -0.013228 | 4.4528e-06 | 3.6656e-08 | 1 | 0
1579 | 26.3167 | 5 | 12 | 5 | 12 | 70.0005 | 40 | 4.3887e-06 | 3.5478 | -6.4125e-08 | 6.1053e-05 | 4.8 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0005 | 35.0002 | 15 | 35 | 0.00022843 | -0.012999 | 4.3887e-06 | 4.0078e-08 | 1 | 0
1580 | 26.3333 | 5 | 12 | 5 | 12 | 70.0005 | 40 | 4.3192e-06 | 3.5478 | -6.9439e-08 | 6.0087e-05 | 4.8 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0005 | 35.0002 | 15 | 35 | 0.00024367 | -0.012756 | 4.3192e-06 | 4.34e-08 | 1 | 0
1581 | 26.35 | 5 | 12 | 5 | 12 | 70.0005 | 40 | 4.2446e-06 | 3.5478 | -7.4588e-08 | 5.905e-05 | 4.8 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0005 | 35.0003 | 15 | 35 | 0.00025837 | -0.012497 | 4.2446e-06 | 4.6617e-08 | 1 | 0
1582 | 26.3667 | 5 | 12 | 5 | 12 | 70.0005 | 40 | 4.1651e-06 | 3.5478 | -7.9565e-08 | 5.7943e-05 | 4.8 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0005 | 35.0003 | 15 | 35 | 0.00027252 | -0.012225 | 4.1651e-06 | 4.9728e-08 | 1 | 0
1583 | 26.3833 | 5 | 12 | 5 | 12 | 70.0006 | 40 | 4.0807e-06 | 3.5479 | -8.4366e-08 | 5.6769e-05 | 4.8 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0006 | 35.0003 | 15 | 35 | 0.00028611 | -0.011939 | 4.0807e-06 | 5.2729e-08 | 1 | 0
1584 | 26.4 | 5 | 12 | 5 | 12 | 70.0006 | 40 | 3.9917e-06 | 3.5479 | -8.8987e-08 | 5.5531e-05 | 4.8 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0006 | 35.0003 | 15 | 35 | 0.00029912 | -0.011639 | 3.9917e-06 | 5.5617e-08 | 1 | 0
1585 | 26.4167 | 5 | 12 | 5 | 12 | 70.0006 | 40 | 3.8983e-06 | 3.5479 | -9.3423e-08 | 5.4232e-05 | 4.8 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0006 | 35.0003 | 15 | 35 | 0.00031154 | -0.011328 | 3.8983e-06 | 5.8389e-08 | 1 | 0
1586 | 26.4333 | 5 | 12 | 5 | 12 | 70.0006 | 40 | 3.8006e-06 | 3.5479 | -9.7671e-08 | 5.2873e-05 | 4.8001 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0006 | 35.0003 | 15 | 35 | 0.00032336 | -0.011005 | 3.8006e-06 | 6.1044e-08 | 1 | 0
1587 | 26.45 | 5 | 12 | 5 | 12 | 70.0007 | 40 | 3.6989e-06 | 3.5479 | -1.0173e-07 | 5.1458e-05 | 4.8001 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0007 | 35.0003 | 15 | 35 | 0.00033458 | -0.01067 | 3.6989e-06 | 6.3579e-08 | 1 | 0
1588 | 26.4667 | 5 | 12 | 5 | 12 | 70.0007 | 40 | 3.5933e-06 | 3.5479 | -1.0559e-07 | 4.9989e-05 | 4.8001 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0007 | 35.0003 | 15 | 35 | 0.00034518 | -0.010325 | 3.5933e-06 | 6.5992e-08 | 1 | 0
1589 | 26.4833 | 5 | 12 | 5 | 12 | 70.0007 | 40 | 3.4841e-06 | 3.5479 | -1.0925e-07 | 4.8469e-05 | 4.8001 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0007 | 35.0004 | 15 | 35 | 0.00035516 | -0.0099696 | 3.4841e-06 | 6.8281e-08 | 1 | 0
1590 | 26.5 | 5 | 12 | 5 | 12 | 70.0007 | 40 | 3.3714e-06 | 3.5479 | -1.1271e-07 | 4.6901e-05 | 4.8001 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0007 | 35.0004 | 15 | 35 | 0.00036451 | -0.0096051 | 3.3714e-06 | 7.0444e-08 | 1 | 0
1591 | 26.5167 | 5 | 12 | 5 | 12 | 70.0007 | 40 | 3.2554e-06 | 3.5479 | -1.1597e-07 | 4.5288e-05 | 4.8001 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0007 | 35.0004 | 15 | 35 | 0.00037323 | -0.0092319 | 3.2554e-06 | 7.2481e-08 | 1 | 0
1592 | 26.5333 | 5 | 12 | 5 | 12 | 70.0008 | 40 | 3.1364e-06 | 3.5479 | -1.1902e-07 | 4.3632e-05 | 4.8001 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0008 | 35.0004 | 15 | 35 | 0.00038132 | -0.0088506 | 3.1364e-06 | 7.439e-08 | 1 | 0
1593 | 26.55 | 5 | 12 | 5 | 12 | 70.0008 | 40 | 3.0145e-06 | 3.5479 | -1.2187e-07 | 4.1936e-05 | 4.8001 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0008 | 35.0004 | 15 | 35 | 0.00038877 | -0.0084618 | 3.0145e-06 | 7.617e-08 | 1 | 0
1594 | 26.5667 | 5 | 12 | 5 | 12 | 70.0008 | 40 | 2.89e-06 | 3.5479 | -1.2451e-07 | 4.0204e-05 | 4.8001 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0008 | 35.0004 | 15 | 35 | 0.00039557 | -0.0080662 | 2.89e-06 | 7.7821e-08 | 1 | 0
1595 | 26.5833 | 5 | 12 | 5 | 12 | 70.0008 | 40 | 2.763e-06 | 3.5479 | -1.2694e-07 | 3.8438e-05 | 4.8001 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0008 | 35.0004 | 15 | 35 | 0.00040174 | -0.0076645 | 2.763e-06 | 7.934e-08 | 1 | 0
1596 | 26.6 | 5 | 12 | 5 | 12 | 70.0008 | 40 | 2.6339e-06 | 3.5479 | -1.2917e-07 | 3.6641e-05 | 4.8001 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0008 | 35.0004 | 15 | 35 | 0.00040726 | -0.0072572 | 2.6339e-06 | 8.0729e-08 | 1 | 0
1597 | 26.6167 | 5 | 12 | 5 | 12 | 70.0008 | 40 | 2.5027e-06 | 3.5479 | -1.3118e-07 | 3.4816e-05 | 4.8001 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0008 | 35.0004 | 15 | 35 | 0.00041214 | -0.0068451 | 2.5027e-06 | 8.1987e-08 | 1 | 0
1598 | 26.6333 | 5 | 12 | 5 | 12 | 70.0008 | 40 | 2.3697e-06 | 3.5479 | -1.3298e-07 | 3.2966e-05 | 4.8001 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0008 | 35.0004 | 15 | 35 | 0.00041637 | -0.0064287 | 2.3697e-06 | 8.3114e-08 | 1 | 0
1599 | 26.65 | 5 | 12 | 5 | 12 | 70.0008 | 40 | 2.2351e-06 | 3.5479 | -1.3457e-07 | 3.1094e-05 | 4.8001 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0008 | 35.0004 | 15 | 35 | 0.00041997 | -0.0060088 | 2.2351e-06 | 8.4109e-08 | 1 | 0
1600 | 26.6667 | 5 | 12 | 5 | 12 | 70.0008 | 40 | 2.0992e-06 | 3.5479 | -1.3596e-07 | 2.9203e-05 | 4.8001 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0008 | 35.0004 | 15 | 35 | 0.00042294 | -0.0055858 | 2.0992e-06 | 8.4974e-08 | 1 | 0
1601 | 26.6833 | 5 | 12 | 5 | 12 | 70.0009 | 40 | 1.962e-06 | 3.5479 | -1.3713e-07 | 2.7295e-05 | 4.8001 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0009 | 35.0004 | 15 | 35 | 0.00042527 | -0.0051606 | 1.962e-06 | 8.5709e-08 | 1 | 0
1602 | 26.7 | 5 | 12 | 5 | 12 | 70.0009 | 40 | 1.8239e-06 | 3.5479 | -1.381e-07 | 2.5374e-05 | 4.8001 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0009 | 35.0004 | 15 | 35 | 0.00042698 | -0.0047336 | 1.8239e-06 | 8.6314e-08 | 1 | 0
1603 | 26.7167 | 5 | 12 | 5 | 12 | 70.0009 | 40 | 1.6851e-06 | 3.5479 | -1.3886e-07 | 2.3442e-05 | 4.8001 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0009 | 35.0004 | 15 | 35 | 0.00042807 | -0.0043055 | 1.6851e-06 | 8.679e-08 | 1 | 0
1604 | 26.7333 | 5 | 12 | 5 | 12 | 70.0009 | 40 | 1.5457e-06 | 3.5479 | -1.3942e-07 | 2.1502e-05 | 4.8001 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0009 | 35.0004 | 15 | 35 | 0.00042854 | -0.003877 | 1.5457e-06 | 8.7139e-08 | 1 | 0
1605 | 26.75 | 5 | 12 | 5 | 12 | 70.0009 | 40 | 1.4059e-06 | 3.5479 | -1.3978e-07 | 1.9558e-05 | 4.8001 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0009 | 35.0004 | 15 | 35 | 0.00042841 | -0.0034486 | 1.4059e-06 | 8.736e-08 | 1 | 0
1606 | 26.7667 | 5 | 12 | 5 | 12 | 70.0009 | 40 | 1.2659e-06 | 3.5479 | -1.3993e-07 | 1.7611e-05 | 4.8001 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0009 | 35.0004 | 15 | 35 | 0.00042768 | -0.0030209 | 1.2659e-06 | 8.7457e-08 | 1 | 0
1607 | 26.7833 | 5 | 12 | 5 | 12 | 70.0009 | 40 | 1.1261e-06 | 3.5479 | -1.3989e-07 | 1.5665e-05 | 4.8001 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0009 | 35.0004 | 15 | 35 | 0.00042636 | -0.0025945 | 1.1261e-06 | 8.743e-08 | 1 | 0
1608 | 26.8 | 5 | 12 | 5 | 12 | 70.0008 | 40 | 9.8641e-07 | 3.5479 | -1.3965e-07 | 1.3723e-05 | 4.8001 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0008 | 35.0004 | 15 | 35 | 0.00042446 | -0.0021701 | 9.8641e-07 | 8.7281e-08 | 1 | 0
1609 | 26.8167 | 5 | 12 | 5 | 12 | 70.0008 | 40 | 8.4719e-07 | 3.5479 | -1.3922e-07 | 1.1786e-05 | 4.8001 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0008 | 35.0004 | 15 | 35 | 0.00042198 | -0.0017481 | 8.4719e-07 | 8.7011e-08 | 1 | 0
1610 | 26.8333 | 5 | 12 | 5 | 12 | 70.0008 | 40 | 7.086e-07 | 3.5479 | -1.386e-07 | 9.8577e-06 | 4.8001 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0008 | 35.0004 | 15 | 35 | 0.00041896 | -0.0013291 | 7.086e-07 | 8.6624e-08 | 1 | 0
1611 | 26.85 | 5 | 12 | 5 | 12 | 70.0008 | 40 | 5.708e-07 | 3.5479 | -1.3779e-07 | 7.9408e-06 | 4.8001 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0008 | 35.0004 | 15 | 35 | 0.00041538 | -0.00091375 | 5.708e-07 | 8.6119e-08 | 1 | 0
1612 | 26.8667 | 5 | 12 | 5 | 12 | 70.0008 | 40 | 4.34e-07 | 3.5479 | -1.368e-07 | 6.0376e-06 | 4.8001 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0008 | 35.0004 | 15 | 35 | 0.00041127 | -0.00050249 | 4.34e-07 | 8.5501e-08 | 1 | 0
1613 | 26.8833 | 5 | 12 | 5 | 12 | 70.0008 | 40 | 2.9837e-07 | 3.5479 | -1.3563e-07 | 4.1508e-06 | 4.8001 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0008 | 35.0004 | 15 | 35 | 0.00040663 | -9.5856e-05 | 2.9837e-07 | 8.4771e-08 | 1 | 0
1614 | 26.9 | 5 | 12 | 5 | 12 | 70.0008 | 40 | 1.6408e-07 | 3.5479 | -1.3429e-07 | 2.2826e-06 | 4.8001 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0008 | 35.0004 | 15 | 35 | 0.00040149 | 0.00030563 | 1.6408e-07 | 8.3932e-08 | 1 | 0
1615 | 26.9167 | 5 | 12 | 5 | 12 | 70.0008 | 40 | 3.13e-08 | 3.5479 | -1.3278e-07 | 4.3543e-07 | 4.8001 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0008 | 35.0004 | 15 | 35 | 0.00039585 | 0.00070148 | 3.13e-08 | 8.2986e-08 | 1 | 0
1616 | 26.9333 | 5 | 12 | 5 | 12 | 70.0008 | 40 | -9.9798e-08 | 3.5479 | -1.311e-07 | -1.3883e-06 | 4.8001 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0008 | 35.0004 | 15 | 35 | 0.00038973 | 0.0010912 | 9.9798e-08 | 8.1936e-08 | 1 | 0
1617 | 26.95 | 5 | 12 | 5 | 12 | 70.0008 | 40 | -2.2905e-07 | 3.5479 | -1.2926e-07 | -3.1865e-06 | 4.8001 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0008 | 35.0004 | 15 | 35 | 0.00038314 | 0.0014743 | 2.2905e-07 | 8.0785e-08 | 1 | 0
1618 | 26.9667 | 5 | 12 | 5 | 12 | 70.0008 | 40 | -3.5631e-07 | 3.5479 | -1.2726e-07 | -4.9568e-06 | 4.8001 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0008 | 35.0004 | 15 | 35 | 0.0003761 | 0.0018504 | 3.5631e-07 | 7.9536e-08 | 1 | 0
1619 | 26.9833 | 5 | 12 | 5 | 12 | 70.0007 | 40 | -4.8142e-07 | 3.5479 | -1.2511e-07 | -6.6973e-06 | 4.8001 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0007 | 35.0004 | 15 | 35 | 0.00036862 | 0.0022191 | 4.8142e-07 | 7.8191e-08 | 1 | 0
1620 | 27 | 5 | 12 | 5 | 12 | 70.0007 | 40 | -6.0423e-07 | 3.5479 | -1.2281e-07 | -8.4057e-06 | 4.8001 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0007 | 35.0004 | 15 | 35 | 0.00036073 | 0.0025798 | 6.0423e-07 | 7.6755e-08 | 1 | 0
1621 | 27.0167 | 5 | 12 | 5 | 12 | 70.0007 | 40 | -7.2459e-07 | 3.5479 | -1.2037e-07 | -1.008e-05 | 4.8001 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0007 | 35.0004 | 15 | 35 | 0.00035243 | 0.0029322 | 7.2459e-07 | 7.523e-08 | 1 | 0
1622 | 27.0333 | 5 | 12 | 5 | 12 | 70.0007 | 40 | -8.4238e-07 | 3.5479 | -1.1779e-07 | -1.1719e-05 | 4.8001 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0007 | 35.0003 | 15 | 35 | 0.00034375 | 0.003276 | 8.4238e-07 | 7.3619e-08 | 1 | 0
1623 | 27.05 | 5 | 12 | 5 | 12 | 70.0007 | 40 | -9.5746e-07 | 3.5479 | -1.1508e-07 | -1.332e-05 | 4.8001 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0007 | 35.0003 | 15 | 35 | 0.0003347 | 0.0036107 | 9.5746e-07 | 7.1925e-08 | 1 | 0
1624 | 27.0667 | 5 | 12 | 5 | 12 | 70.0007 | 40 | -1.0697e-06 | 3.5479 | -1.1225e-07 | -1.4881e-05 | 4.8001 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0007 | 35.0003 | 15 | 35 | 0.0003253 | 0.003936 | 1.0697e-06 | 7.0154e-08 | 1 | 0
1625 | 27.0833 | 5 | 12 | 5 | 12 | 70.0006 | 40 | -1.179e-06 | 3.5479 | -1.0929e-07 | -1.6402e-05 | 4.8001 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0006 | 35.0003 | 15 | 35 | 0.00031556 | 0.0042515 | 1.179e-06 | 6.8306e-08 | 1 | 0
1626 | 27.1 | 5 | 12 | 5 | 12 | 70.0006 | 40 | -1.2852e-06 | 3.5479 | -1.0622e-07 | -1.7879e-05 | 4.8001 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0006 | 35.0003 | 15 | 35 | 0.00030551 | 0.0045571 | 1.2852e-06 | 6.6388e-08 | 1 | 0
1627 | 27.1167 | 5 | 12 | 5 | 12 | 70.0006 | 40 | -1.3883e-06 | 3.5479 | -1.0304e-07 | -1.9313e-05 | 4.8001 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0006 | 35.0003 | 15 | 35 | 0.00029516 | 0.0048522 | 1.3883e-06 | 6.4401e-08 | 1 | 0
1628 | 27.1333 | 5 | 12 | 5 | 12 | 70.0006 | 40 | -1.488e-06 | 3.5479 | -9.9759e-08 | -2.0701e-05 | 4.8001 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0006 | 35.0003 | 15 | 35 | 0.00028453 | 0.0051368 | 1.488e-06 | 6.2349e-08 | 1 | 0
1629 | 27.15 | 5 | 12 | 5 | 12 | 70.0005 | 40 | -1.5844e-06 | 3.5479 | -9.638e-08 | -2.2041e-05 | 4.8001 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0005 | 35.0003 | 15 | 35 | 0.00027365 | 0.0054104 | 1.5844e-06 | 6.0237e-08 | 1 | 0
1630 | 27.1667 | 5 | 12 | 5 | 12 | 70.0005 | 40 | -1.6773e-06 | 3.5479 | -9.2909e-08 | -2.3334e-05 | 4.8001 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0005 | 35.0003 | 15 | 35 | 0.00026252 | 0.0056729 | 1.6773e-06 | 5.8068e-08 | 1 | 0
1631 | 27.1833 | 5 | 12 | 5 | 12 | 70.0005 | 40 | -1.7667e-06 | 3.5479 | -8.9354e-08 | -2.4577e-05 | 4.8001 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0005 | 35.0003 | 15 | 35 | 0.00025116 | 0.0059241 | 1.7667e-06 | 5.5846e-08 | 1 | 0
1632 | 27.2 | 5 | 12 | 5 | 12 | 70.0005 | 40 | -1.8524e-06 | 3.5479 | -8.5719e-08 | -2.577e-05 | 4.8001 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0005 | 35.0002 | 15 | 35 | 0.0002396 | 0.0061637 | 1.8524e-06 | 5.3574e-08 | 1 | 0
1633 | 27.2167 | 5 | 12 | 5 | 12 | 70.0005 | 40 | -1.9344e-06 | 3.5479 | -8.2012e-08 | -2.691e-05 | 4.8001 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0005 | 35.0002 | 15 | 35 | 0.00022786 | 0.0063915 | 1.9344e-06 | 5.1257e-08 | 1 | 0
1634 | 27.2333 | 5 | 12 | 5 | 12 | 70.0004 | 40 | -2.0126e-06 | 3.5479 | -7.8238e-08 | -2.7999e-05 | 4.8001 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0004 | 35.0002 | 15 | 35 | 0.00021595 | 0.0066075 | 2.0126e-06 | 4.8899e-08 | 1 | 0
1635 | 27.25 | 5 | 12 | 5 | 12 | 70.0004 | 40 | -2.087e-06 | 3.5479 | -7.4403e-08 | -2.9034e-05 | 4.8001 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0004 | 35.0002 | 15 | 35 | 0.00020389 | 0.0068114 | 2.087e-06 | 4.6502e-08 | 1 | 0
1636 | 27.2667 | 5 | 12 | 5 | 12 | 70.0004 | 40 | -2.1575e-06 | 3.5479 | -7.0514e-08 | -3.0015e-05 | 4.8001 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0004 | 35.0002 | 15 | 35 | 0.0001917 | 0.0070031 | 2.1575e-06 | 4.4071e-08 | 1 | 0
1637 | 27.2833 | 5 | 12 | 5 | 12 | 70.0004 | 40 | -2.2241e-06 | 3.5479 | -6.6576e-08 | -3.0941e-05 | 4.8001 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0004 | 35.0002 | 15 | 35 | 0.0001794 | 0.0071825 | 2.2241e-06 | 4.161e-08 | 1 | 0
1638 | 27.3 | 5 | 12 | 5 | 12 | 70.0003 | 40 | -2.2867e-06 | 3.5479 | -6.2597e-08 | -3.1812e-05 | 4.8001 | 0 | 4.8001 |  | 15.2001 | 4 | 15.2001 | 70.0003 | 35.0002 | 15 | 35 | 0.00016702 | 0.0073495 | 2.2867e-06 | 3.9123e-08 | 1 | 0
1639 | 27.3167 | 5 | 12 | 5 | 12 | 70.0003 | 40 | -2.3453e-06 | 3.5479 | -5.8581e-08 | -3.2627e-05 | 4.8001 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0003 | 35.0002 | 15 | 35 | 0.00015455 | 0.0075041 | 2.3453e-06 | 3.6613e-08 | 1 | 0
1640 | 27.3333 | 5 | 12 | 5 | 12 | 70.0003 | 40 | -2.3998e-06 | 3.5479 | -5.4536e-08 | -3.3385e-05 | 4.8001 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0003 | 35.0001 | 15 | 35 | 0.00014204 | 0.0076461 | 2.3998e-06 | 3.4085e-08 | 1 | 0
1641 | 27.35 | 5 | 12 | 5 | 12 | 70.0003 | 40 | -2.4503e-06 | 3.5479 | -5.0466e-08 | -3.4088e-05 | 4.8001 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0003 | 35.0001 | 15 | 35 | 0.00012948 | 0.0077756 | 2.4503e-06 | 3.1541e-08 | 1 | 0
1642 | 27.3667 | 5 | 12 | 5 | 12 | 70.0002 | 40 | -2.4967e-06 | 3.5479 | -4.6379e-08 | -3.4733e-05 | 4.8001 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0002 | 35.0001 | 15 | 35 | 0.00011691 | 0.0078925 | 2.4967e-06 | 2.8987e-08 | 1 | 0
1643 | 27.3833 | 5 | 12 | 5 | 12 | 70.0002 | 40 | -2.539e-06 | 3.5479 | -4.228e-08 | -3.5321e-05 | 4.8001 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0002 | 35.0001 | 15 | 35 | 0.00010434 | 0.0079968 | 2.539e-06 | 2.6425e-08 | 1 | 0
1644 | 27.4 | 5 | 12 | 5 | 12 | 70.0002 | 40 | -2.5771e-06 | 3.5479 | -3.8175e-08 | -3.5852e-05 | 4.8001 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0002 | 35.0001 | 15 | 35 | 9.1782e-05 | 0.0080886 | 2.5771e-06 | 2.3859e-08 | 1 | 0
1645 | 27.4167 | 5 | 12 | 5 | 12 | 70.0002 | 40 | -2.6112e-06 | 3.5479 | -3.4069e-08 | -3.6326e-05 | 4.8001 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0002 | 35.0001 | 15 | 35 | 7.926e-05 | 0.0081679 | 2.6112e-06 | 2.1293e-08 | 1 | 0
1646 | 27.4333 | 5 | 12 | 5 | 12 | 70.0001 | 40 | -2.6412e-06 | 3.5479 | -2.997e-08 | -3.6743e-05 | 4.8001 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35.0001 | 15 | 35 | 6.6791e-05 | 0.0082347 | 2.6412e-06 | 1.8731e-08 | 1 | 0
1647 | 27.45 | 5 | 12 | 5 | 12 | 70.0001 | 40 | -2.6671e-06 | 3.5479 | -2.5881e-08 | -3.7103e-05 | 4.8001 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35.0001 | 15 | 35 | 5.439e-05 | 0.008289 | 2.6671e-06 | 1.6176e-08 | 1 | 0
1648 | 27.4667 | 5 | 12 | 5 | 12 | 70.0001 | 40 | -2.6889e-06 | 3.5479 | -2.1809e-08 | -3.7406e-05 | 4.8001 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 4.2073e-05 | 0.0083311 | 2.6889e-06 | 1.3631e-08 | 1 | 0
1649 | 27.4833 | 5 | 12 | 5 | 12 | 70.0001 | 40 | -2.7066e-06 | 3.5479 | -1.776e-08 | -3.7653e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 2.9858e-05 | 0.008361 | 2.7066e-06 | 1.11e-08 | 1 | 0
1650 | 27.5 | 5 | 12 | 5 | 12 | 70 | 40 | -2.7204e-06 | 3.5479 | -1.3738e-08 | -3.7844e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | 1.7759e-05 | 0.0083787 | 2.7204e-06 | 8.5863e-09 | 1 | 0
1651 | 27.5167 | 5 | 12 | 5 | 12 | 70 | 40 | -2.7301e-06 | 3.5479 | -9.7494e-09 | -3.798e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | 5.7922e-06 | 0.0083845 | 2.7301e-06 | 6.0934e-09 | 1 | 0
1652 | 27.5333 | 5 | 12 | 5 | 12 | 70 | 40 | -2.7359e-06 | 3.5479 | -5.7988e-09 | -3.8061e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -6.0272e-06 | 0.0083785 | 2.7359e-06 | 3.6242e-09 | 1 | 0
1653 | 27.55 | 5 | 12 | 5 | 12 | 70 | 40 | -2.7378e-06 | 3.5479 | -1.8913e-09 | -3.8087e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -1.7685e-05 | 0.0083608 | 2.7378e-06 | 1.1821e-09 | 1 | 0
1654 | 27.5667 | 5 | 12 | 5 | 12 | 69.9999 | 40 | -2.7358e-06 | 3.5478 | 1.9681e-09 | -3.806e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 35 | 15 | 35 | -2.9166e-05 | 0.0083316 | 2.7358e-06 | -1.23e-09 | -1 | -2
1655 | 27.5833 | 5 | 12 | 5 | 12 | 69.9999 | 40 | -2.7301e-06 | 3.5478 | 5.7746e-09 | -3.7979e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 35 | 15 | 35 | -4.0458e-05 | 0.0082912 | 2.7301e-06 | -3.6091e-09 | -1 | 0
1656 | 27.6 | 5 | 12 | 5 | 12 | 69.9999 | 40 | -2.7205e-06 | 3.5478 | 9.5236e-09 | -3.7847e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 34.9999 | 15 | 35 | -5.1546e-05 | 0.0082396 | 2.7205e-06 | -5.9523e-09 | -1 | 0
1657 | 27.6167 | 5 | 12 | 5 | 12 | 69.9999 | 40 | -2.7073e-06 | 3.5478 | 1.3211e-08 | -3.7663e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 34.9999 | 15 | 35 | -6.2418e-05 | 0.0081772 | 2.7073e-06 | -8.2566e-09 | -1 | 0
1658 | 27.6333 | 5 | 12 | 5 | 12 | 69.9999 | 40 | -2.6905e-06 | 3.5478 | 1.6831e-08 | -3.7429e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 34.9999 | 15 | 35 | -7.3061e-05 | 0.0081042 | 2.6905e-06 | -1.052e-08 | -1 | 0
1659 | 27.65 | 5 | 12 | 5 | 12 | 69.9998 | 40 | -2.6701e-06 | 3.5478 | 2.0381e-08 | -3.7145e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9998 | 34.9999 | 15 | 35 | -8.3464e-05 | 0.0080207 | 2.6701e-06 | -1.2738e-08 | -1 | 0
1660 | 27.6667 | 5 | 12 | 5 | 12 | 69.9998 | 40 | -2.6463e-06 | 3.5478 | 2.3857e-08 | -3.6814e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9998 | 34.9999 | 15 | 35 | -9.3616e-05 | 0.0079271 | 2.6463e-06 | -1.4911e-08 | -1 | 0
1661 | 27.6833 | 5 | 12 | 5 | 12 | 69.9998 | 40 | -2.619e-06 | 3.5478 | 2.7254e-08 | -3.6434e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9998 | 34.9999 | 15 | 35 | -0.0001035 | 0.0078236 | 2.619e-06 | -1.7034e-08 | -1 | 0
1662 | 27.7 | 5 | 12 | 5 | 12 | 69.9998 | 40 | -2.5884e-06 | 3.5478 | 3.0568e-08 | -3.6009e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9998 | 34.9999 | 15 | 35 | -0.00011312 | 0.0077105 | 2.5884e-06 | -1.9105e-08 | -1 | 0
1663 | 27.7167 | 5 | 12 | 5 | 12 | 69.9998 | 40 | -2.5546e-06 | 3.5478 | 3.3797e-08 | -3.5539e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9998 | 34.9999 | 15 | 35 | -0.00012245 | 0.007588 | 2.5546e-06 | -2.1123e-08 | -1 | 0
1664 | 27.7333 | 5 | 12 | 5 | 12 | 69.9997 | 40 | -2.5177e-06 | 3.5478 | 3.6937e-08 | -3.5025e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9997 | 34.9999 | 15 | 35 | -0.00013149 | 0.0074565 | 2.5177e-06 | -2.3085e-08 | -1 | 0
1665 | 27.75 | 5 | 12 | 5 | 12 | 69.9997 | 40 | -2.4777e-06 | 3.5478 | 3.9984e-08 | -3.4469e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9997 | 34.9999 | 15 | 35 | -0.00014023 | 0.0073163 | 2.4777e-06 | -2.499e-08 | -1 | 0
1666 | 27.7667 | 5 | 12 | 5 | 12 | 69.9997 | 40 | -2.4348e-06 | 3.5478 | 4.2935e-08 | -3.3872e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9997 | 34.9999 | 15 | 35 | -0.00014865 | 0.0071676 | 2.4348e-06 | -2.6835e-08 | -1 | 0
1667 | 27.7833 | 5 | 12 | 5 | 12 | 69.9997 | 40 | -2.389e-06 | 3.5478 | 4.5788e-08 | -3.3235e-05 | 4.8 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9997 | 34.9998 | 15 | 35 | -0.00015676 | 0.0070109 | 2.389e-06 | -2.8618e-08 | -1 | 0
1668 | 27.8 | 5 | 12 | 5 | 12 | 69.9997 | 40 | -2.3405e-06 | 3.5478 | 4.854e-08 | -3.2559e-05 | 4.8 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9997 | 34.9998 | 15 | 35 | -0.00016455 | 0.0068463 | 2.3405e-06 | -3.0338e-08 | -1 | 0
1669 | 27.8167 | 5 | 12 | 5 | 12 | 69.9997 | 40 | -2.2893e-06 | 3.5478 | 5.1188e-08 | -3.1847e-05 | 4.8 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9997 | 34.9998 | 15 | 35 | -0.000172 | 0.0066743 | 2.2893e-06 | -3.1993e-08 | -1 | 0
1670 | 27.8333 | 5 | 12 | 5 | 12 | 69.9996 | 40 | -2.2355e-06 | 3.5478 | 5.373e-08 | -3.11e-05 | 4.8 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9996 | 34.9998 | 15 | 35 | -0.00017912 | 0.0064952 | 2.2355e-06 | -3.3581e-08 | -1 | 0
1671 | 27.85 | 5 | 12 | 5 | 12 | 69.9996 | 40 | -2.1794e-06 | 3.5478 | 5.6164e-08 | -3.0318e-05 | 4.8 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9996 | 34.9998 | 15 | 35 | -0.00018589 | 0.0063093 | 2.1794e-06 | -3.5103e-08 | -1 | 0
1672 | 27.8667 | 5 | 12 | 5 | 12 | 69.9996 | 40 | -2.1209e-06 | 3.5478 | 5.8488e-08 | -2.9505e-05 | 4.8 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9996 | 34.9998 | 15 | 35 | -0.00019232 | 0.006117 | 2.1209e-06 | -3.6555e-08 | -1 | 0
1673 | 27.8833 | 5 | 12 | 5 | 12 | 69.9996 | 40 | -2.0602e-06 | 3.5478 | 6.0699e-08 | -2.866e-05 | 4.8 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9996 | 34.9998 | 15 | 35 | -0.00019839 | 0.0059186 | 2.0602e-06 | -3.7937e-08 | -1 | 0
1674 | 27.9 | 5 | 12 | 5 | 12 | 69.9996 | 40 | -1.9974e-06 | 3.5478 | 6.2797e-08 | -2.7787e-05 | 4.8 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9996 | 34.9998 | 15 | 35 | -0.0002041 | 0.0057145 | 1.9974e-06 | -3.9248e-08 | -1 | 0
1675 | 27.9167 | 5 | 12 | 5 | 12 | 69.9996 | 40 | -1.9326e-06 | 3.5478 | 6.4779e-08 | -2.6886e-05 | 4.8 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9996 | 34.9998 | 15 | 35 | -0.00020946 | 0.0055051 | 1.9326e-06 | -4.0487e-08 | -1 | 0
1676 | 27.9333 | 5 | 12 | 5 | 12 | 69.9996 | 40 | -1.866e-06 | 3.5478 | 6.6645e-08 | -2.5958e-05 | 4.8 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9996 | 34.9998 | 15 | 35 | -0.00021445 | 0.0052906 | 1.866e-06 | -4.1653e-08 | -1 | 0
1677 | 27.95 | 5 | 12 | 5 | 12 | 69.9996 | 40 | -1.7976e-06 | 3.5478 | 6.8394e-08 | -2.5007e-05 | 4.8 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9996 | 34.9998 | 15 | 35 | -0.00021908 | 0.0050715 | 1.7976e-06 | -4.2746e-08 | -1 | 0
1678 | 27.9667 | 5 | 12 | 5 | 12 | 69.9996 | 40 | -1.7275e-06 | 3.5478 | 7.0024e-08 | -2.4033e-05 | 4.8 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9996 | 34.9998 | 15 | 35 | -0.00022333 | 0.0048482 | 1.7275e-06 | -4.3765e-08 | -1 | 0
1679 | 27.9833 | 5 | 12 | 5 | 12 | 69.9995 | 40 | -1.656e-06 | 3.5478 | 7.1535e-08 | -2.3038e-05 | 4.8 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9995 | 34.9998 | 15 | 35 | -0.00022723 | 0.004621 | 1.656e-06 | -4.4709e-08 | -1 | 0
1680 | 28 | 5 | 12 | 5 | 12 | 69.9995 | 40 | -1.5831e-06 | 3.5478 | 7.2926e-08 | -2.2023e-05 | 4.7999 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9995 | 34.9998 | 15 | 35 | -0.00023075 | 0.0043902 | 1.5831e-06 | -4.5579e-08 | -1 | 0
1681 | 28.0167 | 5 | 12 | 5 | 12 | 69.9995 | 40 | -1.5089e-06 | 3.5478 | 7.4196e-08 | -2.0991e-05 | 4.7999 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9995 | 34.9998 | 15 | 35 | -0.0002339 | 0.0041563 | 1.5089e-06 | -4.6373e-08 | -1 | 0
1682 | 28.0333 | 5 | 12 | 5 | 12 | 69.9995 | 40 | -1.4335e-06 | 3.5478 | 7.5347e-08 | -1.9943e-05 | 4.7999 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9995 | 34.9998 | 15 | 35 | -0.00023669 | 0.0039196 | 1.4335e-06 | -4.7092e-08 | -1 | 0
1683 | 28.05 | 5 | 12 | 5 | 12 | 69.9995 | 40 | -1.3572e-06 | 3.5478 | 7.6377e-08 | -1.888e-05 | 4.7999 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9995 | 34.9998 | 15 | 35 | -0.00023911 | 0.0036805 | 1.3572e-06 | -4.7735e-08 | -1 | 0
1684 | 28.0667 | 5 | 12 | 5 | 12 | 69.9995 | 40 | -1.2799e-06 | 3.5478 | 7.7286e-08 | -1.7805e-05 | 4.7999 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9995 | 34.9998 | 15 | 35 | -0.00024116 | 0.0034394 | 1.2799e-06 | -4.8304e-08 | -1 | 0
1685 | 28.0833 | 5 | 12 | 5 | 12 | 69.9995 | 40 | -1.2018e-06 | 3.5478 | 7.8075e-08 | -1.6719e-05 | 4.7999 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9995 | 34.9998 | 15 | 35 | -0.00024284 | 0.0031965 | 1.2018e-06 | -4.8797e-08 | -1 | 0
1686 | 28.1 | 5 | 12 | 5 | 12 | 69.9995 | 40 | -1.1231e-06 | 3.5478 | 7.8745e-08 | -1.5623e-05 | 4.7999 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9995 | 34.9998 | 15 | 35 | -0.00024417 | 0.0029524 | 1.1231e-06 | -4.9216e-08 | -1 | 0
1687 | 28.1167 | 5 | 12 | 5 | 12 | 69.9995 | 40 | -1.0438e-06 | 3.5478 | 7.9296e-08 | -1.452e-05 | 4.7999 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9995 | 34.9998 | 15 | 35 | -0.00024513 | 0.0027072 | 1.0438e-06 | -4.956e-08 | -1 | 0
1688 | 28.1333 | 5 | 12 | 5 | 12 | 69.9995 | 40 | -9.6403e-07 | 3.5478 | 7.9729e-08 | -1.3411e-05 | 4.7999 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9995 | 34.9998 | 15 | 35 | -0.00024574 | 0.0024615 | 9.6403e-07 | -4.983e-08 | -1 | 0
1689 | 28.15 | 5 | 12 | 5 | 12 | 69.9995 | 40 | -8.8399e-07 | 3.5478 | 8.0044e-08 | -1.2298e-05 | 4.7999 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9995 | 34.9998 | 15 | 35 | -0.000246 | 0.0022155 | 8.8399e-07 | -5.0028e-08 | -1 | 0
1690 | 28.1667 | 5 | 12 | 5 | 12 | 69.9995 | 40 | -8.0375e-07 | 3.5478 | 8.0243e-08 | -1.1181e-05 | 4.7999 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9995 | 34.9998 | 15 | 35 | -0.00024591 | 0.0019696 | 8.0375e-07 | -5.0152e-08 | -1 | 0
1691 | 28.1833 | 5 | 12 | 5 | 12 | 69.9995 | 40 | -7.2342e-07 | 3.5478 | 8.0327e-08 | -1.0064e-05 | 4.7999 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9995 | 34.9998 | 15 | 35 | -0.00024548 | 0.0017241 | 7.2342e-07 | -5.0205e-08 | -1 | 0
1692 | 28.2 | 5 | 12 | 5 | 12 | 69.9995 | 40 | -6.4312e-07 | 3.5478 | 8.0298e-08 | -8.9468e-06 | 4.7999 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9995 | 34.9998 | 15 | 35 | -0.00024471 | 0.0014794 | 6.4312e-07 | -5.0186e-08 | -1 | 0
1693 | 28.2167 | 5 | 12 | 5 | 12 | 69.9995 | 40 | -5.6296e-07 | 3.5478 | 8.0156e-08 | -7.8317e-06 | 4.7999 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9995 | 34.9998 | 15 | 35 | -0.0002436 | 0.0012358 | 5.6296e-07 | -5.0098e-08 | -1 | 0
1694 | 28.2333 | 5 | 12 | 5 | 12 | 69.9995 | 40 | -4.8306e-07 | 3.5478 | 7.9904e-08 | -6.7201e-06 | 4.7999 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9995 | 34.9998 | 15 | 35 | -0.00024217 | 0.0009936 | 4.8306e-07 | -4.994e-08 | -1 | 0
1695 | 28.25 | 5 | 12 | 5 | 12 | 69.9995 | 40 | -4.0352e-07 | 3.5478 | 7.9544e-08 | -5.6135e-06 | 4.7999 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9995 | 34.9998 | 15 | 35 | -0.00024042 | 0.00075318 | 4.0352e-07 | -4.9715e-08 | -1 | 0
1696 | 28.2667 | 5 | 12 | 5 | 12 | 69.9995 | 40 | -3.2444e-07 | 3.5478 | 7.9076e-08 | -4.5135e-06 | 4.7999 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9995 | 34.9998 | 15 | 35 | -0.00023835 | 0.00051483 | 3.2444e-07 | -4.9423e-08 | -1 | 0
1697 | 28.2833 | 5 | 12 | 5 | 12 | 69.9995 | 40 | -2.4594e-07 | 3.5478 | 7.8504e-08 | -3.4214e-06 | 4.7999 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9995 | 34.9998 | 15 | 35 | -0.00023598 | 0.00027885 | 2.4594e-07 | -4.9065e-08 | -1 | 0
1698 | 28.3 | 5 | 12 | 5 | 12 | 69.9995 | 40 | -1.6811e-07 | 3.5478 | 7.783e-08 | -2.3386e-06 | 4.7999 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9995 | 34.9998 | 15 | 35 | -0.00023331 | 4.5539e-05 | 1.6811e-07 | -4.8643e-08 | -1 | 0
1699 | 28.3167 | 5 | 12 | 5 | 12 | 69.9995 | 40 | -9.1052e-08 | 3.5478 | 7.7055e-08 | -1.2667e-06 | 4.7999 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9995 | 34.9998 | 15 | 35 | -0.00023034 | -0.0001848 | 9.1052e-08 | -4.8159e-08 | -1 | 0
1700 | 28.3333 | 5 | 12 | 5 | 12 | 69.9995 | 40 | -1.487e-08 | 3.5478 | 7.6182e-08 | -2.0686e-07 | 4.7999 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9995 | 34.9998 | 15 | 35 | -0.00022709 | -0.0004119 | 1.487e-08 | -4.7614e-08 | -1 | 0
1701 | 28.35 | 5 | 12 | 5 | 12 | 69.9996 | 40 | 6.0344e-08 | 3.5478 | 7.5214e-08 | 8.3948e-07 | 4.7999 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9996 | 34.9998 | 15 | 35 | -0.00022357 | -0.00063546 | 6.0344e-08 | -4.7009e-08 | -1 | 0
1702 | 28.3667 | 5 | 12 | 5 | 12 | 69.9996 | 40 | 1.345e-07 | 3.5478 | 7.4153e-08 | 1.8711e-06 | 4.7999 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9996 | 34.9998 | 15 | 35 | -0.00021978 | -0.00085524 | 1.345e-07 | -4.6346e-08 | -1 | 0
1703 | 28.3833 | 5 | 12 | 5 | 12 | 69.9996 | 40 | 2.075e-07 | 3.5478 | 7.3002e-08 | 2.8866e-06 | 4.7999 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9996 | 34.9998 | 15 | 35 | -0.00021572 | -0.001071 | 2.075e-07 | -4.5626e-08 | -1 | 0
1704 | 28.4 | 5 | 12 | 5 | 12 | 69.9996 | 40 | 2.7926e-07 | 3.5478 | 7.1764e-08 | 3.885e-06 | 4.7999 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9996 | 34.9998 | 15 | 35 | -0.00021142 | -0.0012824 | 2.7926e-07 | -4.4852e-08 | -1 | 0
1705 | 28.4167 | 5 | 12 | 5 | 12 | 69.9996 | 40 | 3.497e-07 | 3.5478 | 7.0441e-08 | 4.8649e-06 | 4.7999 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9996 | 34.9998 | 15 | 35 | -0.00020688 | -0.0014893 | 3.497e-07 | -4.4025e-08 | -1 | 0
1706 | 28.4333 | 5 | 12 | 5 | 12 | 69.9996 | 40 | 4.1874e-07 | 3.5478 | 6.9037e-08 | 5.8253e-06 | 4.7999 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9996 | 34.9998 | 15 | 35 | -0.00020211 | -0.0016914 | 4.1874e-07 | -4.3148e-08 | -1 | 0
1707 | 28.45 | 5 | 12 | 5 | 12 | 69.9996 | 40 | 4.8629e-07 | 3.5478 | 6.7554e-08 | 6.7651e-06 | 4.7999 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9996 | 34.9998 | 15 | 35 | -0.00019712 | -0.0018885 | 4.8629e-07 | -4.2221e-08 | -1 | 0
1708 | 28.4667 | 5 | 12 | 5 | 12 | 69.9996 | 40 | 5.5229e-07 | 3.5478 | 6.5996e-08 | 7.6832e-06 | 4.7999 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9996 | 34.9998 | 15 | 35 | -0.00019191 | -0.0020804 | 5.5229e-07 | -4.1247e-08 | -1 | 0
1709 | 28.4833 | 5 | 12 | 5 | 12 | 69.9996 | 40 | 6.1665e-07 | 3.5478 | 6.4365e-08 | 8.5786e-06 | 4.7999 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9996 | 34.9998 | 15 | 35 | -0.00018651 | -0.0022669 | 6.1665e-07 | -4.0228e-08 | -1 | 0
1710 | 28.5 | 5 | 12 | 5 | 12 | 69.9996 | 40 | 6.7932e-07 | 3.5478 | 6.2666e-08 | 9.4504e-06 | 4.7999 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9996 | 34.9998 | 15 | 35 | -0.00018091 | -0.0024478 | 6.7932e-07 | -3.9166e-08 | -1 | 0
1711 | 28.5167 | 5 | 12 | 5 | 12 | 69.9996 | 40 | 7.4022e-07 | 3.5478 | 6.0901e-08 | 1.0298e-05 | 4.7999 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9996 | 34.9998 | 15 | 35 | -0.00017514 | -0.002623 | 7.4022e-07 | -3.8063e-08 | -1 | 0
1712 | 28.5333 | 5 | 12 | 5 | 12 | 69.9997 | 40 | 7.993e-07 | 3.5478 | 5.9074e-08 | 1.1119e-05 | 4.7999 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9997 | 34.9998 | 15 | 35 | -0.00016919 | -0.0027922 | 7.993e-07 | -3.6921e-08 | -1 | 0
1713 | 28.55 | 5 | 12 | 5 | 12 | 69.9997 | 40 | 8.5648e-07 | 3.5478 | 5.7187e-08 | 1.1915e-05 | 4.7999 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9997 | 34.9998 | 15 | 35 | -0.00016308 | -0.0029552 | 8.5648e-07 | -3.5742e-08 | -1 | 0
1714 | 28.5667 | 5 | 12 | 5 | 12 | 69.9997 | 40 | 9.1173e-07 | 3.5478 | 5.5245e-08 | 1.2684e-05 | 4.7999 | 0 | 4.7999 |  | 15.1999 | 4 | 15.1999 | 69.9997 | 34.9998 | 15 | 35 | -0.00015682 | -0.0031121 | 9.1173e-07 | -3.4528e-08 | -1 | 0
1715 | 28.5833 | 5 | 12 | 5 | 12 | 69.9997 | 40 | 9.6498e-07 | 3.5478 | 5.3251e-08 | 1.3424e-05 | 4.7999 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9997 | 34.9998 | 15 | 35 | -0.00015043 | -0.0032625 | 9.6498e-07 | -3.3282e-08 | -1 | 0
1716 | 28.6 | 5 | 12 | 5 | 12 | 69.9997 | 40 | 1.0162e-06 | 3.5478 | 5.1208e-08 | 1.4137e-05 | 4.7999 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9997 | 34.9999 | 15 | 35 | -0.00014391 | -0.0034064 | 1.0162e-06 | -3.2005e-08 | -1 | 0
1717 | 28.6167 | 5 | 12 | 5 | 12 | 69.9997 | 40 | 1.0653e-06 | 3.5478 | 4.912e-08 | 1.482e-05 | 4.7999 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9997 | 34.9999 | 15 | 35 | -0.00013727 | -0.0035437 | 1.0653e-06 | -3.07e-08 | -1 | 0
1718 | 28.6333 | 5 | 12 | 5 | 12 | 69.9997 | 40 | 1.1123e-06 | 3.5478 | 4.699e-08 | 1.5474e-05 | 4.7999 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9997 | 34.9999 | 15 | 35 | -0.00013052 | -0.0036742 | 1.1123e-06 | -2.9369e-08 | -1 | 0
1719 | 28.65 | 5 | 12 | 5 | 12 | 69.9998 | 40 | 1.1571e-06 | 3.5478 | 4.4822e-08 | 1.6097e-05 | 4.7999 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9998 | 34.9999 | 15 | 35 | -0.00012368 | -0.0037979 | 1.1571e-06 | -2.8014e-08 | -1 | 0
1720 | 28.6667 | 5 | 12 | 5 | 12 | 69.9998 | 40 | 1.1997e-06 | 3.5478 | 4.2619e-08 | 1.669e-05 | 4.7999 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9998 | 34.9999 | 15 | 35 | -0.00011676 | -0.0039146 | 1.1997e-06 | -2.6637e-08 | -1 | 0
1721 | 28.6833 | 5 | 12 | 5 | 12 | 69.9998 | 40 | 1.2401e-06 | 3.5478 | 4.0386e-08 | 1.7252e-05 | 4.7999 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9998 | 34.9999 | 15 | 35 | -0.00010976 | -0.0040244 | 1.2401e-06 | -2.5241e-08 | -1 | 0
1722 | 28.7 | 5 | 12 | 5 | 12 | 69.9998 | 40 | 1.2782e-06 | 3.5478 | 3.8124e-08 | 1.7782e-05 | 4.7999 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9998 | 34.9999 | 15 | 35 | -0.0001027 | -0.0041271 | 1.2782e-06 | -2.3828e-08 | -1 | 0
1723 | 28.7167 | 5 | 12 | 5 | 12 | 69.9998 | 40 | 1.3141e-06 | 3.5478 | 3.5839e-08 | 1.8281e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9998 | 34.9999 | 15 | 35 | -9.5582e-05 | -0.0042227 | 1.3141e-06 | -2.2399e-08 | -1 | 0
1724 | 28.7333 | 5 | 12 | 5 | 12 | 69.9998 | 40 | 1.3476e-06 | 3.5478 | 3.3533e-08 | 1.8748e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9998 | 34.9999 | 15 | 35 | -8.8426e-05 | -0.0043111 | 1.3476e-06 | -2.0958e-08 | -1 | 0
1725 | 28.75 | 5 | 12 | 5 | 12 | 69.9998 | 40 | 1.3788e-06 | 3.5478 | 3.121e-08 | 1.9182e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9998 | 34.9999 | 15 | 35 | -8.124e-05 | -0.0043923 | 1.3788e-06 | -1.9506e-08 | -1 | 0
1726 | 28.7667 | 5 | 12 | 5 | 12 | 69.9999 | 40 | 1.4077e-06 | 3.5478 | 2.8874e-08 | 1.9583e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 34.9999 | 15 | 35 | -7.4033e-05 | -0.0044664 | 1.4077e-06 | -1.8046e-08 | -1 | 0
1727 | 28.7833 | 5 | 12 | 5 | 12 | 69.9999 | 40 | 1.4342e-06 | 3.5478 | 2.6527e-08 | 1.9952e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 34.9999 | 15 | 35 | -6.6816e-05 | -0.0045332 | 1.4342e-06 | -1.658e-08 | -1 | 0
1728 | 28.8 | 5 | 12 | 5 | 12 | 69.9999 | 40 | 1.4584e-06 | 3.5478 | 2.4174e-08 | 2.0289e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 34.9999 | 15 | 35 | -5.9599e-05 | -0.0045928 | 1.4584e-06 | -1.5109e-08 | -1 | 0
1729 | 28.8167 | 5 | 12 | 5 | 12 | 69.9999 | 40 | 1.4802e-06 | 3.5478 | 2.1817e-08 | 2.0592e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 34.9999 | 15 | 35 | -5.2392e-05 | -0.0046452 | 1.4802e-06 | -1.3636e-08 | -1 | 0
1730 | 28.8333 | 5 | 12 | 5 | 12 | 69.9999 | 40 | 1.4997e-06 | 3.5478 | 1.9461e-08 | 2.0863e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 35 | 15 | 35 | -4.5205e-05 | -0.0046904 | 1.4997e-06 | -1.2163e-08 | -1 | 0
1731 | 28.85 | 5 | 12 | 5 | 12 | 69.9999 | 40 | 1.5168e-06 | 3.5478 | 1.7108e-08 | 2.1101e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 35 | 15 | 35 | -3.8049e-05 | -0.0047284 | 1.5168e-06 | -1.0692e-08 | -1 | 0
1732 | 28.8667 | 5 | 12 | 5 | 12 | 69.9999 | 40 | 1.5316e-06 | 3.5478 | 1.4761e-08 | 2.1306e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 35 | 15 | 35 | -3.0932e-05 | -0.0047594 | 1.5316e-06 | -9.2256e-09 | -1 | 0
1733 | 28.8833 | 5 | 12 | 5 | 12 | 70 | 40 | 1.544e-06 | 3.5478 | 1.2424e-08 | 2.1479e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -2.3864e-05 | -0.0047832 | 1.544e-06 | -7.765e-09 | -1 | 0
1734 | 28.9 | 5 | 12 | 5 | 12 | 70 | 40 | 1.5541e-06 | 3.5478 | 1.01e-08 | 2.162e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -1.6854e-05 | -0.0048001 | 1.5541e-06 | -6.3126e-09 | -1 | 0
1735 | 28.9167 | 5 | 12 | 5 | 12 | 70 | 40 | 1.5619e-06 | 3.5478 | 7.7922e-09 | 2.1728e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -9.9117e-06 | -0.00481 | 1.5619e-06 | -4.8701e-09 | -1 | 0
1736 | 28.9333 | 5 | 12 | 5 | 12 | 70 | 40 | 1.5674e-06 | 3.5478 | 5.5033e-09 | 2.1805e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -3.0457e-06 | -0.004813 | 1.5674e-06 | -3.4396e-09 | -1 | 0
1737 | 28.95 | 5 | 12 | 5 | 12 | 70 | 40 | 1.5706e-06 | 3.5478 | 3.2365e-09 | 2.185e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | 3.7354e-06 | -0.0048093 | 1.5706e-06 | -2.0228e-09 | -1 | 0
1738 | 28.9667 | 5 | 12 | 5 | 12 | 70 | 40 | 1.5716e-06 | 3.5478 | 9.9452e-10 | 2.1863e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | 1.0423e-05 | -0.0047989 | 1.5716e-06 | -6.2157e-10 | -1 | 0
1739 | 28.9833 | 5 | 12 | 5 | 12 | 70 | 40 | 1.5704e-06 | 3.5478 | -1.2197e-09 | 2.1846e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | 1.701e-05 | -0.0047819 | 1.5704e-06 | 7.6234e-10 | 1 | 2
1740 | 29 | 5 | 12 | 5 | 12 | 70 | 40 | 1.567e-06 | 3.5478 | -3.4035e-09 | 2.1799e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | 2.3487e-05 | -0.0047584 | 1.567e-06 | 2.1272e-09 | 1 | 0
1741 | 29.0167 | 5 | 12 | 5 | 12 | 70.0001 | 40 | 1.5614e-06 | 3.5478 | -5.5542e-09 | 2.1722e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 2.9847e-05 | -0.0047285 | 1.5614e-06 | 3.4714e-09 | 1 | 0
1742 | 29.0333 | 5 | 12 | 5 | 12 | 70.0001 | 40 | 1.5538e-06 | 3.5478 | -7.6692e-09 | 2.1615e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 3.6083e-05 | -0.0046925 | 1.5538e-06 | 4.7932e-09 | 1 | 0
1743 | 29.05 | 5 | 12 | 5 | 12 | 70.0001 | 40 | 1.544e-06 | 3.5478 | -9.746e-09 | 2.148e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 4.2187e-05 | -0.0046503 | 1.544e-06 | 6.0912e-09 | 1 | 0
1744 | 29.0667 | 5 | 12 | 5 | 12 | 70.0001 | 40 | 1.5322e-06 | 3.5478 | -1.1782e-08 | 2.1316e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 4.8153e-05 | -0.0046021 | 1.5322e-06 | 7.3638e-09 | 1 | 0
1745 | 29.0833 | 5 | 12 | 5 | 12 | 70.0001 | 40 | 1.5185e-06 | 3.5478 | -1.3775e-08 | 2.1124e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35.0001 | 15 | 35 | 5.3974e-05 | -0.0045481 | 1.5185e-06 | 8.6096e-09 | 1 | 0
1746 | 29.1 | 5 | 12 | 5 | 12 | 70.0001 | 40 | 1.5027e-06 | 3.5478 | -1.5723e-08 | 2.0905e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35.0001 | 15 | 35 | 5.9644e-05 | -0.0044885 | 1.5027e-06 | 9.8272e-09 | 1 | 0
1747 | 29.1167 | 5 | 12 | 5 | 12 | 70.0001 | 40 | 1.4851e-06 | 3.5478 | -1.7624e-08 | 2.066e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35.0001 | 15 | 35 | 6.5157e-05 | -0.0044233 | 1.4851e-06 | 1.1015e-08 | 1 | 0
1748 | 29.1333 | 5 | 12 | 5 | 12 | 70.0001 | 40 | 1.4656e-06 | 3.5478 | -1.9476e-08 | 2.0389e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35.0001 | 15 | 35 | 7.0507e-05 | -0.0043528 | 1.4656e-06 | 1.2172e-08 | 1 | 0
1749 | 29.15 | 5 | 12 | 5 | 12 | 70.0002 | 40 | 1.4444e-06 | 3.5478 | -2.1276e-08 | 2.0093e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0002 | 35.0001 | 15 | 35 | 7.5688e-05 | -0.0042771 | 1.4444e-06 | 1.3297e-08 | 1 | 0
1750 | 29.1667 | 5 | 12 | 5 | 12 | 70.0002 | 40 | 1.4213e-06 | 3.5478 | -2.3023e-08 | 1.9773e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0002 | 35.0001 | 15 | 35 | 8.0697e-05 | -0.0041964 | 1.4213e-06 | 1.4389e-08 | 1 | 0
1751 | 29.1833 | 5 | 12 | 5 | 12 | 70.0002 | 40 | 1.3966e-06 | 3.5478 | -2.4715e-08 | 1.9429e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0002 | 35.0001 | 15 | 35 | 8.5527e-05 | -0.0041109 | 1.3966e-06 | 1.5447e-08 | 1 | 0
1752 | 29.2 | 5 | 12 | 5 | 12 | 70.0002 | 40 | 1.3703e-06 | 3.5478 | -2.635e-08 | 1.9063e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0002 | 35.0001 | 15 | 35 | 9.0175e-05 | -0.0040207 | 1.3703e-06 | 1.6469e-08 | 1 | 0
1753 | 29.2167 | 5 | 12 | 5 | 12 | 70.0002 | 40 | 1.3423e-06 | 3.5478 | -2.7927e-08 | 1.8674e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0002 | 35.0001 | 15 | 35 | 9.4636e-05 | -0.0039261 | 1.3423e-06 | 1.7455e-08 | 1 | 0
1754 | 29.2333 | 5 | 12 | 5 | 12 | 70.0002 | 40 | 1.3129e-06 | 3.5478 | -2.9445e-08 | 1.8264e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0002 | 35.0001 | 15 | 35 | 9.8907e-05 | -0.0038272 | 1.3129e-06 | 1.8403e-08 | 1 | 0
1755 | 29.25 | 5 | 12 | 5 | 12 | 70.0002 | 40 | 1.282e-06 | 3.5478 | -3.0902e-08 | 1.7835e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0002 | 35.0001 | 15 | 35 | 0.00010298 | -0.0037242 | 1.282e-06 | 1.9314e-08 | 1 | 0
1756 | 29.2667 | 5 | 12 | 5 | 12 | 70.0002 | 40 | 1.2497e-06 | 3.5478 | -3.2296e-08 | 1.7385e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0002 | 35.0001 | 15 | 35 | 0.00010686 | -0.0036173 | 1.2497e-06 | 2.0185e-08 | 1 | 0
1757 | 29.2833 | 5 | 12 | 5 | 12 | 70.0002 | 40 | 1.2161e-06 | 3.5478 | -3.3627e-08 | 1.6917e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0002 | 35.0001 | 15 | 35 | 0.00011054 | -0.0035068 | 1.2161e-06 | 2.1017e-08 | 1 | 0
1758 | 29.3 | 5 | 12 | 5 | 12 | 70.0002 | 40 | 1.1812e-06 | 3.5478 | -3.4894e-08 | 1.6432e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0002 | 35.0001 | 15 | 35 | 0.00011402 | -0.0033928 | 1.1812e-06 | 2.1809e-08 | 1 | 0
1759 | 29.3167 | 5 | 12 | 5 | 12 | 70.0002 | 40 | 1.1451e-06 | 3.5478 | -3.6096e-08 | 1.593e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0002 | 35.0001 | 15 | 35 | 0.00011729 | -0.0032755 | 1.1451e-06 | 2.256e-08 | 1 | 0
1760 | 29.3333 | 5 | 12 | 5 | 12 | 70.0002 | 40 | 1.1078e-06 | 3.5478 | -3.7231e-08 | 1.5412e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0002 | 35.0001 | 15 | 35 | 0.00012036 | -0.0031551 | 1.1078e-06 | 2.3269e-08 | 1 | 0
1761 | 29.35 | 5 | 12 | 5 | 12 | 70.0002 | 40 | 1.0695e-06 | 3.5478 | -3.8299e-08 | 1.4879e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0002 | 35.0001 | 15 | 35 | 0.00012321 | -0.0030319 | 1.0695e-06 | 2.3937e-08 | 1 | 0
1762 | 29.3667 | 5 | 12 | 5 | 12 | 70.0003 | 40 | 1.0302e-06 | 3.5478 | -3.93e-08 | 1.4332e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0003 | 35.0001 | 15 | 35 | 0.00012586 | -0.0029061 | 1.0302e-06 | 2.4563e-08 | 1 | 0
1763 | 29.3833 | 5 | 12 | 5 | 12 | 70.0003 | 40 | 9.9002e-07 | 3.5478 | -4.0233e-08 | 1.3773e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0003 | 35.0001 | 15 | 35 | 0.0001283 | -0.0027778 | 9.9002e-07 | 2.5146e-08 | 1 | 0
1764 | 29.4 | 5 | 12 | 5 | 12 | 70.0003 | 40 | 9.4892e-07 | 3.5478 | -4.1098e-08 | 1.3201e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0003 | 35.0001 | 15 | 35 | 0.00013052 | -0.0026472 | 9.4892e-07 | 2.5686e-08 | 1 | 0
1765 | 29.4167 | 5 | 12 | 5 | 12 | 70.0003 | 40 | 9.0702e-07 | 3.5478 | -4.1893e-08 | 1.2618e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0003 | 35.0001 | 15 | 35 | 0.00013254 | -0.0025147 | 9.0702e-07 | 2.6183e-08 | 1 | 0
1766 | 29.4333 | 5 | 12 | 5 | 12 | 70.0003 | 40 | 8.644e-07 | 3.5478 | -4.262e-08 | 1.2025e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0003 | 35.0001 | 15 | 35 | 0.00013434 | -0.0023804 | 8.644e-07 | 2.6637e-08 | 1 | 0
1767 | 29.45 | 5 | 12 | 5 | 12 | 70.0003 | 40 | 8.2113e-07 | 3.5478 | -4.3278e-08 | 1.1423e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0003 | 35.0001 | 15 | 35 | 0.00013593 | -0.0022444 | 8.2113e-07 | 2.7048e-08 | 1 | 0
1768 | 29.4667 | 5 | 12 | 5 | 12 | 70.0003 | 40 | 7.7726e-07 | 3.5479 | -4.3866e-08 | 1.0813e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0003 | 35.0001 | 15 | 35 | 0.00013731 | -0.0021071 | 7.7726e-07 | 2.7416e-08 | 1 | 0
1769 | 29.4833 | 5 | 12 | 5 | 12 | 70.0003 | 40 | 7.3288e-07 | 3.5479 | -4.4385e-08 | 1.0195e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0003 | 35.0001 | 15 | 35 | 0.00013848 | -0.0019686 | 7.3288e-07 | 2.7741e-08 | 1 | 0
1770 | 29.5 | 5 | 12 | 5 | 12 | 70.0003 | 40 | 6.8804e-07 | 3.5479 | -4.4835e-08 | 9.5717e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0003 | 35.0001 | 15 | 35 | 0.00013944 | -0.0018292 | 6.8804e-07 | 2.8022e-08 | 1 | 0
1771 | 29.5167 | 5 | 12 | 5 | 12 | 70.0003 | 40 | 6.4282e-07 | 3.5479 | -4.5217e-08 | 8.9427e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0003 | 35.0001 | 15 | 35 | 0.00014019 | -0.001689 | 6.4282e-07 | 2.8261e-08 | 1 | 0
1772 | 29.5333 | 5 | 12 | 5 | 12 | 70.0003 | 40 | 5.9729e-07 | 3.5479 | -4.5531e-08 | 8.3093e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0003 | 35.0001 | 15 | 35 | 0.00014074 | -0.0015483 | 5.9729e-07 | 2.8457e-08 | 1 | 0
1773 | 29.55 | 5 | 12 | 5 | 12 | 70.0003 | 40 | 5.5152e-07 | 3.5479 | -4.5776e-08 | 7.6725e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0003 | 35.0001 | 15 | 35 | 0.00014108 | -0.0014072 | 5.5152e-07 | 2.861e-08 | 1 | 0
1774 | 29.5667 | 5 | 12 | 5 | 12 | 70.0003 | 40 | 5.0556e-07 | 3.5479 | -4.5954e-08 | 7.0332e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0003 | 35.0001 | 15 | 35 | 0.00014122 | -0.001266 | 5.0556e-07 | 2.8722e-08 | 1 | 0
1775 | 29.5833 | 5 | 12 | 5 | 12 | 70.0003 | 40 | 4.595e-07 | 3.5479 | -4.6066e-08 | 6.3923e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0003 | 35.0001 | 15 | 35 | 0.00014116 | -0.0011248 | 4.595e-07 | 2.8791e-08 | 1 | 0
1776 | 29.6 | 5 | 12 | 5 | 12 | 70.0003 | 40 | 4.1338e-07 | 3.5479 | -4.6112e-08 | 5.7508e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0003 | 35.0001 | 15 | 35 | 0.0001409 | -0.00098393 | 4.1338e-07 | 2.882e-08 | 1 | 0
1777 | 29.6167 | 5 | 12 | 5 | 12 | 70.0003 | 40 | 3.6729e-07 | 3.5479 | -4.6092e-08 | 5.1096e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0003 | 35.0001 | 15 | 35 | 0.00014045 | -0.00084348 | 3.6729e-07 | 2.8808e-08 | 1 | 0
1778 | 29.6333 | 5 | 12 | 5 | 12 | 70.0003 | 40 | 3.2128e-07 | 3.5479 | -4.6008e-08 | 4.4696e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0003 | 35.0001 | 15 | 35 | 0.00013981 | -0.00070368 | 3.2128e-07 | 2.8755e-08 | 1 | 0
1779 | 29.65 | 5 | 12 | 5 | 12 | 70.0003 | 40 | 2.7542e-07 | 3.5479 | -4.5861e-08 | 3.8316e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0003 | 35.0001 | 15 | 35 | 0.00013898 | -0.0005647 | 2.7542e-07 | 2.8663e-08 | 1 | 0
1780 | 29.6667 | 5 | 12 | 5 | 12 | 70.0003 | 40 | 2.2977e-07 | 3.5479 | -4.5651e-08 | 3.1965e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0003 | 35.0001 | 15 | 35 | 0.00013796 | -0.00042673 | 2.2977e-07 | 2.8532e-08 | 1 | 0
1781 | 29.6833 | 5 | 12 | 5 | 12 | 70.0003 | 40 | 1.8439e-07 | 3.5479 | -4.5381e-08 | 2.5652e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0003 | 35.0001 | 15 | 35 | 0.00013677 | -0.00028996 | 1.8439e-07 | 2.8363e-08 | 1 | 0
1782 | 29.7 | 5 | 12 | 5 | 12 | 70.0003 | 40 | 1.3934e-07 | 3.5479 | -4.505e-08 | 1.9385e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0003 | 35.0001 | 15 | 35 | 0.0001354 | -0.00015456 | 1.3934e-07 | 2.8156e-08 | 1 | 0
1783 | 29.7167 | 5 | 12 | 5 | 12 | 70.0003 | 40 | 9.4681e-08 | 3.5479 | -4.466e-08 | 1.3172e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0003 | 35.0001 | 15 | 35 | 0.00013386 | -2.0698e-05 | 9.4681e-08 | 2.7913e-08 | 1 | 0
1784 | 29.7333 | 5 | 12 | 5 | 12 | 70.0003 | 40 | 5.0468e-08 | 3.5479 | -4.4213e-08 | 7.0209e-07 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0003 | 35.0001 | 15 | 35 | 0.00013215 | 0.00011145 | 5.0468e-08 | 2.7633e-08 | 1 | 0
1785 | 29.75 | 5 | 12 | 5 | 12 | 70.0003 | 40 | 6.7586e-09 | 3.5479 | -4.371e-08 | 9.4023e-08 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0003 | 35.0001 | 15 | 35 | 0.00013028 | 0.00024173 | 6.7586e-09 | 2.7319e-08 | 1 | 0
1786 | 29.7667 | 5 | 12 | 5 | 12 | 70.0003 | 40 | -3.6393e-08 | 3.5479 | -4.3152e-08 | -5.0629e-07 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0003 | 35.0001 | 15 | 35 | 0.00012825 | 0.00036999 | 3.6393e-08 | 2.697e-08 | 1 | 0
1787 | 29.7833 | 5 | 12 | 5 | 12 | 70.0003 | 40 | -7.8934e-08 | 3.5479 | -4.2541e-08 | -1.0981e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0003 | 35.0001 | 15 | 35 | 0.00012607 | 0.00049605 | 7.8934e-08 | 2.6588e-08 | 1 | 0
1788 | 29.8 | 5 | 12 | 5 | 12 | 70.0002 | 40 | -1.2081e-07 | 3.5479 | -4.1878e-08 | -1.6807e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0002 | 35.0001 | 15 | 35 | 0.00012374 | 0.00061979 | 1.2081e-07 | 2.6174e-08 | 1 | 0
1789 | 29.8167 | 5 | 12 | 5 | 12 | 70.0002 | 40 | -1.6198e-07 | 3.5479 | -4.1165e-08 | -2.2533e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0002 | 35.0001 | 15 | 35 | 0.00012126 | 0.00074105 | 1.6198e-07 | 2.5728e-08 | 1 | 0
1790 | 29.8333 | 5 | 12 | 5 | 12 | 70.0002 | 40 | -2.0238e-07 | 3.5479 | -4.0404e-08 | -2.8154e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0002 | 35.0001 | 15 | 35 | 0.00011865 | 0.0008597 | 2.0238e-07 | 2.5252e-08 | 1 | 0
1791 | 29.85 | 5 | 12 | 5 | 12 | 70.0002 | 40 | -2.4198e-07 | 3.5479 | -3.9596e-08 | -3.3663e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0002 | 35.0001 | 15 | 35 | 0.00011591 | 0.00097561 | 2.4198e-07 | 2.4747e-08 | 1 | 0
1792 | 29.8667 | 5 | 12 | 5 | 12 | 70.0002 | 40 | -2.8072e-07 | 3.5479 | -3.8743e-08 | -3.9052e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0002 | 35.0001 | 15 | 35 | 0.00011303 | 0.0010886 | 2.8072e-07 | 2.4214e-08 | 1 | 0
1793 | 29.8833 | 5 | 12 | 5 | 12 | 70.0002 | 40 | -3.1857e-07 | 3.5479 | -3.7847e-08 | -4.4317e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0002 | 35.0001 | 15 | 35 | 0.00011004 | 0.0011987 | 3.1857e-07 | 2.3654e-08 | 1 | 0
1794 | 29.9 | 5 | 12 | 5 | 12 | 70.0002 | 40 | -3.5547e-07 | 3.5479 | -3.6909e-08 | -4.9452e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0002 | 35.0001 | 15 | 35 | 0.00010693 | 0.0013056 | 3.5547e-07 | 2.3068e-08 | 1 | 0
1795 | 29.9167 | 5 | 12 | 5 | 12 | 70.0002 | 40 | -3.9141e-07 | 3.5479 | -3.5932e-08 | -5.4451e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0002 | 35.0001 | 15 | 35 | 0.00010372 | 0.0014093 | 3.9141e-07 | 2.2458e-08 | 1 | 0
1796 | 29.9333 | 5 | 12 | 5 | 12 | 70.0002 | 40 | -4.2632e-07 | 3.5479 | -3.4917e-08 | -5.9308e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0002 | 35.0001 | 15 | 35 | 0.0001004 | 0.0015097 | 4.2632e-07 | 2.1823e-08 | 1 | 0
1797 | 29.95 | 5 | 12 | 5 | 12 | 70.0002 | 40 | -4.6019e-07 | 3.5479 | -3.3867e-08 | -6.402e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0002 | 35.0001 | 15 | 35 | 9.6979e-05 | 0.0016067 | 4.6019e-07 | 2.1167e-08 | 1 | 0
1798 | 29.9667 | 5 | 12 | 5 | 12 | 70.0002 | 40 | -4.9297e-07 | 3.5479 | -3.2783e-08 | -6.858e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0002 | 35.0001 | 15 | 35 | 9.347e-05 | 0.0017002 | 4.9297e-07 | 2.0489e-08 | 1 | 0
1799 | 29.9833 | 5 | 12 | 5 | 12 | 70.0002 | 40 | -5.2464e-07 | 3.5479 | -3.1667e-08 | -7.2986e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0002 | 35.0001 | 15 | 35 | 8.9875e-05 | 0.0017901 | 5.2464e-07 | 1.9792e-08 | 1 | 0
1800 | 30 | 5 | 12 | 5 | 12 | 70.0002 | 40 | -5.5516e-07 | 3.5479 | -3.0521e-08 | -7.7232e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0002 | 35.0001 | 15 | 35 | 8.6201e-05 | 0.0018763 | 5.5516e-07 | 1.9075e-08 | 1 | 0
1801 | 30.0167 | 5 | 12 | 5 | 12 | 70.0002 | 40 | -5.8451e-07 | 3.5479 | -2.9347e-08 | -8.1314e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0002 | 35.0001 | 15 | 35 | 8.2454e-05 | 0.0019587 | 5.8451e-07 | 1.8342e-08 | 1 | 0
1802 | 30.0333 | 5 | 12 | 5 | 12 | 70.0002 | 40 | -6.1266e-07 | 3.5479 | -2.8147e-08 | -8.523e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0002 | 35.0001 | 15 | 35 | 7.864e-05 | 0.0020374 | 6.1266e-07 | 1.7592e-08 | 1 | 0
1803 | 30.05 | 5 | 12 | 5 | 12 | 70.0001 | 40 | -6.3958e-07 | 3.5479 | -2.6924e-08 | -8.8975e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35.0001 | 15 | 35 | 7.4765e-05 | 0.0021121 | 6.3958e-07 | 1.6827e-08 | 1 | 0
1804 | 30.0667 | 5 | 12 | 5 | 12 | 70.0001 | 40 | -6.6526e-07 | 3.5478 | -2.5678e-08 | -9.2548e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35.0001 | 15 | 35 | 7.0836e-05 | 0.002183 | 6.6526e-07 | 1.6049e-08 | 1 | 0
1805 | 30.0833 | 5 | 12 | 5 | 12 | 70.0001 | 40 | -6.8967e-07 | 3.5478 | -2.4413e-08 | -9.5944e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35.0001 | 15 | 35 | 6.6859e-05 | 0.0022498 | 6.8967e-07 | 1.5258e-08 | 1 | 0
1806 | 30.1 | 5 | 12 | 5 | 12 | 70.0001 | 40 | -7.128e-07 | 3.5478 | -2.313e-08 | -9.9162e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35.0001 | 15 | 35 | 6.284e-05 | 0.0023127 | 7.128e-07 | 1.4456e-08 | 1 | 0
1807 | 30.1167 | 5 | 12 | 5 | 12 | 70.0001 | 40 | -7.3463e-07 | 3.5478 | -2.1832e-08 | -1.022e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35.0001 | 15 | 35 | 5.8785e-05 | 0.0023714 | 7.3463e-07 | 1.3645e-08 | 1 | 0
1808 | 30.1333 | 5 | 12 | 5 | 12 | 70.0001 | 40 | -7.5515e-07 | 3.5478 | -2.0519e-08 | -1.0505e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35.0001 | 15 | 35 | 5.47e-05 | 0.0024261 | 7.5515e-07 | 1.2824e-08 | 1 | 0
1809 | 30.15 | 5 | 12 | 5 | 12 | 70.0001 | 40 | -7.7435e-07 | 3.5478 | -1.9195e-08 | -1.0772e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35.0001 | 15 | 35 | 5.0592e-05 | 0.0024767 | 7.7435e-07 | 1.1997e-08 | 1 | 0
1810 | 30.1667 | 5 | 12 | 5 | 12 | 70.0001 | 40 | -7.9221e-07 | 3.5478 | -1.7861e-08 | -1.1021e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 4.6466e-05 | 0.0025232 | 7.9221e-07 | 1.1163e-08 | 1 | 0
1811 | 30.1833 | 5 | 12 | 5 | 12 | 70.0001 | 40 | -8.0873e-07 | 3.5478 | -1.652e-08 | -1.1251e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 4.2328e-05 | 0.0025655 | 8.0873e-07 | 1.0325e-08 | 1 | 0
1812 | 30.2 | 5 | 12 | 5 | 12 | 70.0001 | 40 | -8.239e-07 | 3.5478 | -1.5172e-08 | -1.1462e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 3.8185e-05 | 0.0026037 | 8.239e-07 | 9.4828e-09 | 1 | 0
1813 | 30.2167 | 5 | 12 | 5 | 12 | 70.0001 | 40 | -8.3772e-07 | 3.5478 | -1.3821e-08 | -1.1654e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 3.4043e-05 | 0.0026377 | 8.3772e-07 | 8.6384e-09 | 1 | 0
1814 | 30.2333 | 5 | 12 | 5 | 12 | 70.0001 | 40 | -8.5019e-07 | 3.5478 | -1.2469e-08 | -1.1827e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 2.9906e-05 | 0.0026677 | 8.5019e-07 | 7.7929e-09 | 1 | 0
1815 | 30.25 | 5 | 12 | 5 | 12 | 70.0001 | 40 | -8.6131e-07 | 3.5478 | -1.1116e-08 | -1.1982e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 2.5781e-05 | 0.0026934 | 8.6131e-07 | 6.9475e-09 | 1 | 0
1816 | 30.2667 | 5 | 12 | 5 | 12 | 70 | 40 | -8.7107e-07 | 3.5478 | -9.7652e-09 | -1.2118e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | 2.1674e-05 | 0.0027151 | 8.7107e-07 | 6.1033e-09 | 1 | 0
1817 | 30.2833 | 5 | 12 | 5 | 12 | 70 | 40 | -8.7949e-07 | 3.5478 | -8.4183e-09 | -1.2235e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | 1.7589e-05 | 0.0027327 | 8.7949e-07 | 5.2615e-09 | 1 | 0
1818 | 30.3 | 5 | 12 | 5 | 12 | 70 | 40 | -8.8657e-07 | 3.5478 | -7.0772e-09 | -1.2334e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | 1.3533e-05 | 0.0027462 | 8.8657e-07 | 4.4232e-09 | 1 | 0
1819 | 30.3167 | 5 | 12 | 5 | 12 | 70 | 40 | -8.9231e-07 | 3.5478 | -5.7435e-09 | -1.2413e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | 9.511e-06 | 0.0027557 | 8.9231e-07 | 3.5897e-09 | 1 | 0
1820 | 30.3333 | 5 | 12 | 5 | 12 | 70 | 40 | -8.9673e-07 | 3.5478 | -4.4191e-09 | -1.2475e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | 5.5276e-06 | 0.0027613 | 8.9673e-07 | 2.7619e-09 | 1 | 0
1821 | 30.35 | 5 | 12 | 5 | 12 | 70 | 40 | -8.9983e-07 | 3.5478 | -3.1056e-09 | -1.2518e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | 1.5881e-06 | 0.0027629 | 8.9983e-07 | 1.941e-09 | 1 | 0
1822 | 30.3667 | 5 | 12 | 5 | 12 | 70 | 40 | -9.0164e-07 | 3.5478 | -1.8049e-09 | -1.2543e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -2.3024e-06 | 0.0027606 | 9.0164e-07 | 1.1281e-09 | 1 | 0
1823 | 30.3833 | 5 | 12 | 5 | 12 | 70 | 40 | -9.0216e-07 | 3.5478 | -5.1858e-10 | -1.255e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -6.1392e-06 | 0.0027544 | 9.0216e-07 | 3.2411e-10 | 1 | 0
1824 | 30.4 | 5 | 12 | 5 | 12 | 70 | 40 | -9.0141e-07 | 3.5478 | 7.518e-10 | -1.254e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -9.9176e-06 | 0.0027445 | 9.0141e-07 | -4.6988e-10 | -1 | -2
1825 | 30.4167 | 5 | 12 | 5 | 12 | 70 | 40 | -8.994e-07 | 3.5478 | 2.0046e-09 | -1.2512e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -1.3633e-05 | 0.0027309 | 8.994e-07 | -1.2529e-09 | -1 | 0
1826 | 30.4333 | 5 | 12 | 5 | 12 | 70 | 40 | -8.9616e-07 | 3.5478 | 3.2384e-09 | -1.2467e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -1.7281e-05 | 0.0027136 | 8.9616e-07 | -2.024e-09 | -1 | 0
1827 | 30.45 | 5 | 12 | 5 | 12 | 70 | 40 | -8.9171e-07 | 3.5478 | 4.4516e-09 | -1.2405e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -2.0858e-05 | 0.0026927 | 8.9171e-07 | -2.7823e-09 | -1 | 0
1828 | 30.4667 | 5 | 12 | 5 | 12 | 70 | 40 | -8.8607e-07 | 3.5478 | 5.6429e-09 | -1.2327e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -2.4359e-05 | 0.0026684 | 8.8607e-07 | -3.5268e-09 | -1 | 0
1829 | 30.4833 | 5 | 12 | 5 | 12 | 69.9999 | 40 | -8.7926e-07 | 3.5478 | 6.8107e-09 | -1.2232e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 35 | 15 | 35 | -2.778e-05 | 0.0026406 | 8.7926e-07 | -4.2567e-09 | -1 | 0
1830 | 30.5 | 5 | 12 | 5 | 12 | 69.9999 | 40 | -8.713e-07 | 3.5478 | 7.9539e-09 | -1.2121e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 35 | 15 | 35 | -3.1118e-05 | 0.0026095 | 8.713e-07 | -4.9712e-09 | -1 | 0
1831 | 30.5167 | 5 | 12 | 5 | 12 | 69.9999 | 40 | -8.6223e-07 | 3.5478 | 9.0711e-09 | -1.1995e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 35 | 15 | 35 | -3.4369e-05 | 0.0025751 | 8.6223e-07 | -5.6694e-09 | -1 | 0
1832 | 30.5333 | 5 | 12 | 5 | 12 | 69.9999 | 40 | -8.5207e-07 | 3.5478 | 1.0161e-08 | -1.1854e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 35 | 15 | 35 | -3.753e-05 | 0.0025376 | 8.5207e-07 | -6.3506e-09 | -1 | 0
1833 | 30.55 | 5 | 12 | 5 | 12 | 69.9999 | 40 | -8.4085e-07 | 3.5478 | 1.1223e-08 | -1.1698e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 35 | 15 | 35 | -4.0597e-05 | 0.002497 | 8.4085e-07 | -7.0141e-09 | -1 | 0
1834 | 30.5667 | 5 | 12 | 5 | 12 | 69.9999 | 40 | -8.2859e-07 | 3.5478 | 1.2255e-08 | -1.1527e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 35 | 15 | 35 | -4.3568e-05 | 0.0024534 | 8.2859e-07 | -7.6592e-09 | -1 | 0
1835 | 30.5833 | 5 | 12 | 5 | 12 | 69.9999 | 40 | -8.1534e-07 | 3.5478 | 1.3256e-08 | -1.1343e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 35 | 15 | 35 | -4.6439e-05 | 0.002407 | 8.1534e-07 | -8.2851e-09 | -1 | 0
1836 | 30.6 | 5 | 12 | 5 | 12 | 69.9999 | 40 | -8.0111e-07 | 3.5478 | 1.4226e-08 | -1.1145e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 35 | 15 | 35 | -4.9207e-05 | 0.0023578 | 8.0111e-07 | -8.8914e-09 | -1 | 0
1837 | 30.6167 | 5 | 12 | 5 | 12 | 69.9999 | 40 | -7.8595e-07 | 3.5478 | 1.5164e-08 | -1.0934e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 34.9999 | 15 | 35 | -5.1871e-05 | 0.0023059 | 7.8595e-07 | -9.4773e-09 | -1 | 0
1838 | 30.6333 | 5 | 12 | 5 | 12 | 69.9999 | 40 | -7.6988e-07 | 3.5478 | 1.6068e-08 | -1.071e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 34.9999 | 15 | 35 | -5.4427e-05 | 0.0022515 | 7.6988e-07 | -1.0042e-08 | -1 | 0
1839 | 30.65 | 5 | 12 | 5 | 12 | 69.9999 | 40 | -7.5294e-07 | 3.5478 | 1.6937e-08 | -1.0475e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 34.9999 | 15 | 35 | -5.6874e-05 | 0.0021946 | 7.5294e-07 | -1.0586e-08 | -1 | 0
1840 | 30.6667 | 5 | 12 | 5 | 12 | 69.9999 | 40 | -7.3517e-07 | 3.5478 | 1.7772e-08 | -1.0227e-05 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 34.9999 | 15 | 35 | -5.921e-05 | 0.0021354 | 7.3517e-07 | -1.1108e-08 | -1 | 0
1841 | 30.6833 | 5 | 12 | 5 | 12 | 69.9999 | 40 | -7.166e-07 | 3.5478 | 1.8571e-08 | -9.969e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 34.9999 | 15 | 35 | -6.1433e-05 | 0.0020739 | 7.166e-07 | -1.1607e-08 | -1 | 0
1842 | 30.7 | 5 | 12 | 5 | 12 | 69.9999 | 40 | -6.9727e-07 | 3.5478 | 1.9334e-08 | -9.7001e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 34.9999 | 15 | 35 | -6.354e-05 | 0.0020104 | 6.9727e-07 | -1.2084e-08 | -1 | 0
1843 | 30.7167 | 5 | 12 | 5 | 12 | 69.9999 | 40 | -6.7721e-07 | 3.5478 | 2.006e-08 | -9.421e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 34.9999 | 15 | 35 | -6.5531e-05 | 0.0019449 | 6.7721e-07 | -1.2537e-08 | -1 | 0
1844 | 30.7333 | 5 | 12 | 5 | 12 | 69.9999 | 40 | -6.5646e-07 | 3.5478 | 2.0748e-08 | -9.1324e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 34.9999 | 15 | 35 | -6.7405e-05 | 0.0018775 | 6.5646e-07 | -1.2967e-08 | -1 | 0
1845 | 30.75 | 5 | 12 | 5 | 12 | 69.9999 | 40 | -6.3506e-07 | 3.5478 | 2.1398e-08 | -8.8347e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 34.9999 | 15 | 35 | -6.9159e-05 | 0.0018083 | 6.3506e-07 | -1.3374e-08 | -1 | 0
1846 | 30.7667 | 5 | 12 | 5 | 12 | 69.9999 | 40 | -6.1305e-07 | 3.5478 | 2.201e-08 | -8.5285e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 34.9999 | 15 | 35 | -7.0794e-05 | 0.0017375 | 6.1305e-07 | -1.3756e-08 | -1 | 0
1847 | 30.7833 | 5 | 12 | 5 | 12 | 69.9999 | 40 | -5.9047e-07 | 3.5478 | 2.2583e-08 | -8.2143e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 34.9999 | 15 | 35 | -7.2309e-05 | 0.0016652 | 5.9047e-07 | -1.4114e-08 | -1 | 0
1848 | 30.8 | 5 | 12 | 5 | 12 | 69.9999 | 40 | -5.6735e-07 | 3.5478 | 2.3117e-08 | -7.8928e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 34.9999 | 15 | 35 | -7.3703e-05 | 0.0015915 | 5.6735e-07 | -1.4448e-08 | -1 | 0
1849 | 30.8167 | 5 | 12 | 5 | 12 | 69.9999 | 40 | -5.4374e-07 | 3.5478 | 2.3611e-08 | -7.5643e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 34.9999 | 15 | 35 | -7.4975e-05 | 0.0015165 | 5.4374e-07 | -1.4757e-08 | -1 | 0
1850 | 30.8333 | 5 | 12 | 5 | 12 | 69.9998 | 40 | -5.1967e-07 | 3.5478 | 2.4066e-08 | -7.2295e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9998 | 34.9999 | 15 | 35 | -7.6126e-05 | 0.0014404 | 5.1967e-07 | -1.5041e-08 | -1 | 0
1851 | 30.85 | 5 | 12 | 5 | 12 | 69.9998 | 40 | -4.9519e-07 | 3.5478 | 2.4482e-08 | -6.8889e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9998 | 34.9999 | 15 | 35 | -7.7156e-05 | 0.0013632 | 4.9519e-07 | -1.5301e-08 | -1 | 0
1852 | 30.8667 | 5 | 12 | 5 | 12 | 69.9998 | 40 | -4.7034e-07 | 3.5478 | 2.4858e-08 | -6.5431e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9998 | 34.9999 | 15 | 35 | -7.8064e-05 | 0.0012852 | 4.7034e-07 | -1.5536e-08 | -1 | 0
1853 | 30.8833 | 5 | 12 | 5 | 12 | 69.9998 | 40 | -4.4514e-07 | 3.5478 | 2.5194e-08 | -6.1926e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9998 | 34.9999 | 15 | 35 | -7.885e-05 | 0.0012063 | 4.4514e-07 | -1.5746e-08 | -1 | 0
1854 | 30.9 | 5 | 12 | 5 | 12 | 69.9998 | 40 | -4.1965e-07 | 3.5478 | 2.549e-08 | -5.838e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9998 | 34.9999 | 15 | 35 | -7.9516e-05 | 0.0011268 | 4.1965e-07 | -1.5931e-08 | -1 | 0
1855 | 30.9167 | 5 | 12 | 5 | 12 | 69.9998 | 40 | -3.939e-07 | 3.5478 | 2.5747e-08 | -5.4798e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9998 | 34.9999 | 15 | 35 | -8.0063e-05 | 0.0010468 | 3.939e-07 | -1.6092e-08 | -1 | 0
1856 | 30.9333 | 5 | 12 | 5 | 12 | 69.9998 | 40 | -3.6794e-07 | 3.5478 | 2.5965e-08 | -5.1186e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9998 | 34.9999 | 15 | 35 | -8.0489e-05 | 0.00096626 | 3.6794e-07 | -1.6228e-08 | -1 | 0
1857 | 30.95 | 5 | 12 | 5 | 12 | 69.9998 | 40 | -3.418e-07 | 3.5478 | 2.6143e-08 | -4.7549e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9998 | 34.9999 | 15 | 35 | -8.0798e-05 | 0.00088547 | 3.418e-07 | -1.6339e-08 | -1 | 0
1858 | 30.9667 | 5 | 12 | 5 | 12 | 69.9998 | 40 | -3.1551e-07 | 3.5478 | 2.6282e-08 | -4.3893e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9998 | 34.9999 | 15 | 35 | -8.0989e-05 | 0.00080448 | 3.1551e-07 | -1.6426e-08 | -1 | 0
1859 | 30.9833 | 5 | 12 | 5 | 12 | 69.9998 | 40 | -2.8913e-07 | 3.5478 | 2.6383e-08 | -4.0223e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9998 | 34.9999 | 15 | 35 | -8.1065e-05 | 0.00072341 | 2.8913e-07 | -1.6489e-08 | -1 | 0
1860 | 31 | 5 | 12 | 5 | 12 | 69.9998 | 40 | -2.6269e-07 | 3.5478 | 2.6446e-08 | -3.6544e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9998 | 34.9999 | 15 | 35 | -8.1026e-05 | 0.00064239 | 2.6269e-07 | -1.6528e-08 | -1 | 0
1861 | 31.0167 | 5 | 12 | 5 | 12 | 69.9998 | 40 | -2.3622e-07 | 3.5478 | 2.647e-08 | -3.2861e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9998 | 34.9999 | 15 | 35 | -8.0874e-05 | 0.00056151 | 2.3622e-07 | -1.6544e-08 | -1 | 0
1862 | 31.0333 | 5 | 12 | 5 | 12 | 69.9998 | 40 | -2.0976e-07 | 3.5478 | 2.6457e-08 | -2.9181e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9998 | 34.9999 | 15 | 35 | -8.061e-05 | 0.0004809 | 2.0976e-07 | -1.6536e-08 | -1 | 0
1863 | 31.05 | 5 | 12 | 5 | 12 | 69.9998 | 40 | -1.8335e-07 | 3.5478 | 2.6408e-08 | -2.5507e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9998 | 34.9999 | 15 | 35 | -8.0238e-05 | 0.00040066 | 1.8335e-07 | -1.6505e-08 | -1 | 0
1864 | 31.0667 | 5 | 12 | 5 | 12 | 69.9998 | 40 | -1.5703e-07 | 3.5478 | 2.6322e-08 | -2.1845e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9998 | 34.9999 | 15 | 35 | -7.9757e-05 | 0.00032091 | 1.5703e-07 | -1.6451e-08 | -1 | 0
1865 | 31.0833 | 5 | 12 | 5 | 12 | 69.9998 | 40 | -1.3083e-07 | 3.5478 | 2.62e-08 | -1.82e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9998 | 34.9999 | 15 | 35 | -7.9171e-05 | 0.00024174 | 1.3083e-07 | -1.6375e-08 | -1 | 0
1866 | 31.1 | 5 | 12 | 5 | 12 | 69.9998 | 40 | -1.0479e-07 | 3.5478 | 2.6043e-08 | -1.4577e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9998 | 34.9999 | 15 | 35 | -7.8482e-05 | 0.00016325 | 1.0479e-07 | -1.6277e-08 | -1 | 0
1867 | 31.1167 | 5 | 12 | 5 | 12 | 69.9998 | 40 | -7.8934e-08 | 3.5478 | 2.5852e-08 | -1.0981e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9998 | 34.9999 | 15 | 35 | -7.7692e-05 | 8.5562e-05 | 7.8934e-08 | -1.6157e-08 | -1 | 0
1868 | 31.1333 | 5 | 12 | 5 | 12 | 69.9998 | 40 | -5.3307e-08 | 3.5478 | 2.5627e-08 | -7.4159e-07 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9998 | 34.9999 | 15 | 35 | -7.6803e-05 | 8.7589e-06 | 5.3307e-08 | -1.6017e-08 | -1 | 0
1869 | 31.15 | 5 | 12 | 5 | 12 | 69.9998 | 40 | -2.7939e-08 | 3.5478 | 2.5369e-08 | -3.8867e-07 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9998 | 34.9999 | 15 | 35 | -7.5818e-05 | -6.706e-05 | 2.7939e-08 | -1.5856e-08 | -1 | 0
1870 | 31.1667 | 5 | 12 | 5 | 12 | 69.9999 | 40 | -2.86e-09 | 3.5478 | 2.5079e-08 | -3.9788e-08 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 34.9999 | 15 | 35 | -7.474e-05 | -0.0001418 | 2.86e-09 | -1.5674e-08 | -1 | 0
1871 | 31.1833 | 5 | 12 | 5 | 12 | 69.9999 | 40 | 2.1897e-08 | 3.5478 | 2.4757e-08 | 3.0462e-07 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 34.9999 | 15 | 35 | -7.3571e-05 | -0.00021537 | 2.1897e-08 | -1.5473e-08 | -1 | 0
1872 | 31.2 | 5 | 12 | 5 | 12 | 69.9999 | 40 | 4.6302e-08 | 3.5478 | 2.4405e-08 | 6.4413e-07 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 34.9999 | 15 | 35 | -7.2315e-05 | -0.00028769 | 4.6302e-08 | -1.5253e-08 | -1 | 0
1873 | 31.2167 | 5 | 12 | 5 | 12 | 69.9999 | 40 | 7.0325e-08 | 3.5478 | 2.4023e-08 | 9.7834e-07 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 34.9999 | 15 | 35 | -7.0973e-05 | -0.00035866 | 7.0325e-08 | -1.5015e-08 | -1 | 0
1874 | 31.2333 | 5 | 12 | 5 | 12 | 69.9999 | 40 | 9.3938e-08 | 3.5478 | 2.3613e-08 | 1.3068e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 34.9999 | 15 | 35 | -6.9549e-05 | -0.00042821 | 9.3938e-08 | -1.4758e-08 | -1 | 0
1875 | 31.25 | 5 | 12 | 5 | 12 | 69.9999 | 40 | 1.1711e-07 | 3.5478 | 2.3175e-08 | 1.6292e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 34.9999 | 15 | 35 | -6.8047e-05 | -0.00049626 | 1.1711e-07 | -1.4484e-08 | -1 | 0
1876 | 31.2667 | 5 | 12 | 5 | 12 | 69.9999 | 40 | 1.3982e-07 | 3.5478 | 2.271e-08 | 1.9452e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 34.9999 | 15 | 35 | -6.6468e-05 | -0.00056272 | 1.3982e-07 | -1.4194e-08 | -1 | 0
1877 | 31.2833 | 5 | 12 | 5 | 12 | 69.9999 | 40 | 1.6204e-07 | 3.5478 | 2.2219e-08 | 2.2543e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 34.9999 | 15 | 35 | -6.4817e-05 | -0.00062754 | 1.6204e-07 | -1.3887e-08 | -1 | 0
1878 | 31.3 | 5 | 12 | 5 | 12 | 69.9999 | 40 | 1.8375e-07 | 3.5478 | 2.1704e-08 | 2.5562e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 34.9999 | 15 | 35 | -6.3097e-05 | -0.00069064 | 1.8375e-07 | -1.3565e-08 | -1 | 0
1879 | 31.3167 | 5 | 12 | 5 | 12 | 69.9999 | 40 | 2.0491e-07 | 3.5478 | 2.1165e-08 | 2.8506e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 34.9999 | 15 | 35 | -6.131e-05 | -0.00075195 | 2.0491e-07 | -1.3228e-08 | -1 | 0
1880 | 31.3333 | 5 | 12 | 5 | 12 | 69.9999 | 40 | 2.2551e-07 | 3.5478 | 2.0603e-08 | 3.1373e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 34.9999 | 15 | 35 | -5.9461e-05 | -0.00081141 | 2.2551e-07 | -1.2877e-08 | -1 | 0
1881 | 31.35 | 5 | 12 | 5 | 12 | 69.9999 | 40 | 2.4553e-07 | 3.5478 | 2.002e-08 | 3.4158e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 34.9999 | 15 | 35 | -5.7553e-05 | -0.00086896 | 2.4553e-07 | -1.2512e-08 | -1 | 0
1882 | 31.3667 | 5 | 12 | 5 | 12 | 69.9999 | 40 | 2.6495e-07 | 3.5478 | 1.9416e-08 | 3.6859e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 34.9999 | 15 | 35 | -5.5588e-05 | -0.00092455 | 2.6495e-07 | -1.2135e-08 | -1 | 0
1883 | 31.3833 | 5 | 12 | 5 | 12 | 69.9999 | 40 | 2.8374e-07 | 3.5478 | 1.8793e-08 | 3.9473e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 34.9999 | 15 | 35 | -5.3572e-05 | -0.00097812 | 2.8374e-07 | -1.1745e-08 | -1 | 0
1884 | 31.4 | 5 | 12 | 5 | 12 | 69.9999 | 40 | 3.0189e-07 | 3.5478 | 1.8151e-08 | 4.1998e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 34.9999 | 15 | 35 | -5.1506e-05 | -0.0010296 | 3.0189e-07 | -1.1345e-08 | -1 | 0
1885 | 31.4167 | 5 | 12 | 5 | 12 | 69.9999 | 40 | 3.1939e-07 | 3.5478 | 1.7493e-08 | 4.4432e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 35 | 15 | 35 | -4.9395e-05 | -0.001079 | 3.1939e-07 | -1.0933e-08 | -1 | 0
1886 | 31.4333 | 5 | 12 | 5 | 12 | 69.9999 | 40 | 3.3621e-07 | 3.5478 | 1.6818e-08 | 4.6771e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 35 | 15 | 35 | -4.7243e-05 | -0.0011263 | 3.3621e-07 | -1.0511e-08 | -1 | 0
1887 | 31.45 | 5 | 12 | 5 | 12 | 69.9999 | 40 | 3.5233e-07 | 3.5478 | 1.6129e-08 | 4.9015e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 35 | 15 | 35 | -4.5052e-05 | -0.0011713 | 3.5233e-07 | -1.0081e-08 | -1 | 0
1888 | 31.4667 | 5 | 12 | 5 | 12 | 69.9999 | 40 | 3.6776e-07 | 3.5478 | 1.5426e-08 | 5.1161e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 35 | 15 | 35 | -4.2827e-05 | -0.0012141 | 3.6776e-07 | -9.6414e-09 | -1 | 0
1889 | 31.4833 | 5 | 12 | 5 | 12 | 69.9999 | 40 | 3.8247e-07 | 3.5478 | 1.4711e-08 | 5.3208e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 35 | 15 | 35 | -4.057e-05 | -0.0012547 | 3.8247e-07 | -9.1943e-09 | -1 | 0
1890 | 31.5 | 5 | 12 | 5 | 12 | 69.9999 | 40 | 3.9646e-07 | 3.5478 | 1.3984e-08 | 5.5153e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 35 | 15 | 35 | -3.8286e-05 | -0.001293 | 3.9646e-07 | -8.7401e-09 | -1 | 0
1891 | 31.5167 | 5 | 12 | 5 | 12 | 69.9999 | 40 | 4.097e-07 | 3.5478 | 1.3247e-08 | 5.6996e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 35 | 15 | 35 | -3.5978e-05 | -0.001329 | 4.097e-07 | -8.2796e-09 | -1 | 0
1892 | 31.5333 | 5 | 12 | 5 | 12 | 69.9999 | 40 | 4.222e-07 | 3.5478 | 1.2501e-08 | 5.8735e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 35 | 15 | 35 | -3.3649e-05 | -0.0013626 | 4.222e-07 | -7.8134e-09 | -1 | 0
1893 | 31.55 | 5 | 12 | 5 | 12 | 69.9999 | 40 | 4.3395e-07 | 3.5478 | 1.1748e-08 | 6.0369e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 35 | 15 | 35 | -3.1304e-05 | -0.0013939 | 4.3395e-07 | -7.3424e-09 | -1 | 0
1894 | 31.5667 | 5 | 12 | 5 | 12 | 69.9999 | 40 | 4.4494e-07 | 3.5478 | 1.0987e-08 | 6.1898e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 35 | 15 | 35 | -2.8945e-05 | -0.0014229 | 4.4494e-07 | -6.8672e-09 | -1 | 0
1895 | 31.5833 | 5 | 12 | 5 | 12 | 69.9999 | 40 | 4.5516e-07 | 3.5478 | 1.0222e-08 | 6.332e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 35 | 15 | 35 | -2.6576e-05 | -0.0014495 | 4.5516e-07 | -6.3885e-09 | -1 | 0
1896 | 31.6 | 5 | 12 | 5 | 12 | 70 | 40 | 4.6461e-07 | 3.5478 | 9.4514e-09 | 6.4635e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -2.4201e-05 | -0.0014737 | 4.6461e-07 | -5.9071e-09 | -1 | 0
1897 | 31.6167 | 5 | 12 | 5 | 12 | 70 | 40 | 4.7329e-07 | 3.5478 | 8.6779e-09 | 6.5842e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -2.1823e-05 | -0.0014955 | 4.7329e-07 | -5.4237e-09 | -1 | 0
1898 | 31.6333 | 5 | 12 | 5 | 12 | 70 | 40 | 4.8119e-07 | 3.5478 | 7.9023e-09 | 6.6941e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -1.9445e-05 | -0.0015149 | 4.8119e-07 | -4.9389e-09 | -1 | 0
1899 | 31.65 | 5 | 12 | 5 | 12 | 70 | 40 | 4.8832e-07 | 3.5478 | 7.1257e-09 | 6.7933e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -1.707e-05 | -0.001532 | 4.8832e-07 | -4.4536e-09 | -1 | 0
1900 | 31.6667 | 5 | 12 | 5 | 12 | 70 | 40 | 4.9467e-07 | 3.5478 | 6.3492e-09 | 6.8816e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -1.4703e-05 | -0.0015467 | 4.9467e-07 | -3.9683e-09 | -1 | 0
1901 | 31.6833 | 5 | 12 | 5 | 12 | 70 | 40 | 5.0024e-07 | 3.5478 | 5.5739e-09 | 6.9591e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -1.2345e-05 | -0.001559 | 5.0024e-07 | -3.4837e-09 | -1 | 0
1902 | 31.7 | 5 | 12 | 5 | 12 | 70 | 40 | 5.0504e-07 | 3.5478 | 4.8009e-09 | 7.0259e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -1.0001e-05 | -0.001569 | 5.0504e-07 | -3.0006e-09 | -1 | 0
1903 | 31.7167 | 5 | 12 | 5 | 12 | 70 | 40 | 5.0907e-07 | 3.5478 | 4.0312e-09 | 7.082e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -7.6738e-06 | -0.0015767 | 5.0907e-07 | -2.5195e-09 | -1 | 0
1904 | 31.7333 | 5 | 12 | 5 | 12 | 70 | 40 | 5.1234e-07 | 3.5478 | 3.2658e-09 | 7.1274e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -5.3657e-06 | -0.0015821 | 5.1234e-07 | -2.0411e-09 | -1 | 0
1905 | 31.75 | 5 | 12 | 5 | 12 | 70 | 40 | 5.1485e-07 | 3.5478 | 2.5057e-09 | 7.1623e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -3.0801e-06 | -0.0015852 | 5.1485e-07 | -1.5661e-09 | -1 | 0
1906 | 31.7667 | 5 | 12 | 5 | 12 | 70 | 40 | 5.166e-07 | 3.5478 | 1.7521e-09 | 7.1867e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -8.1974e-07 | -0.001586 | 5.166e-07 | -1.095e-09 | -1 | 0
1907 | 31.7833 | 5 | 12 | 5 | 12 | 70 | 40 | 5.176e-07 | 3.5478 | 1.0057e-09 | 7.2007e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | 1.4124e-06 | -0.0015846 | 5.176e-07 | -6.2858e-10 | -1 | 0
1908 | 31.8 | 5 | 12 | 5 | 12 | 70 | 40 | 5.1787e-07 | 3.5478 | 2.6767e-10 | 7.2044e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | 3.6135e-06 | -0.001581 | 5.1787e-07 | -1.6729e-10 | -1 | 0
1909 | 31.8167 | 5 | 12 | 5 | 12 | 70 | 40 | 5.1741e-07 | 3.5478 | -4.6118e-10 | 7.198e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | 5.7811e-06 | -0.0015752 | 5.1741e-07 | 2.8824e-10 | 1 | 2
1910 | 31.8333 | 5 | 12 | 5 | 12 | 70 | 40 | 5.1623e-07 | 3.5478 | -1.1799e-09 | 7.1816e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | 7.9124e-06 | -0.0015673 | 5.1623e-07 | 7.3746e-10 | 1 | 0
1911 | 31.85 | 5 | 12 | 5 | 12 | 70 | 40 | 5.1434e-07 | 3.5478 | -1.8877e-09 | 7.1553e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | 1.0005e-05 | -0.0015573 | 5.1434e-07 | 1.1798e-09 | 1 | 0
1912 | 31.8667 | 5 | 12 | 5 | 12 | 70 | 40 | 5.1176e-07 | 3.5478 | -2.5836e-09 | 7.1194e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | 1.2056e-05 | -0.0015452 | 5.1176e-07 | 1.6148e-09 | 1 | 0
1913 | 31.8833 | 5 | 12 | 5 | 12 | 70 | 40 | 5.0849e-07 | 3.5478 | -3.2669e-09 | 7.0739e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | 1.4064e-05 | -0.0015311 | 5.0849e-07 | 2.0418e-09 | 1 | 0
1914 | 31.9 | 5 | 12 | 5 | 12 | 70 | 40 | 5.0455e-07 | 3.5478 | -3.9367e-09 | 7.0191e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | 1.6026e-05 | -0.0015151 | 5.0455e-07 | 2.4605e-09 | 1 | 0
1915 | 31.9167 | 5 | 12 | 5 | 12 | 70 | 40 | 4.9996e-07 | 3.5478 | -4.5924e-09 | 6.9553e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | 1.794e-05 | -0.0014972 | 4.9996e-07 | 2.8702e-09 | 1 | 0
1916 | 31.9333 | 5 | 12 | 5 | 12 | 70 | 40 | 4.9473e-07 | 3.5478 | -5.233e-09 | 6.8825e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | 1.9805e-05 | -0.0014774 | 4.9473e-07 | 3.2707e-09 | 1 | 0
1917 | 31.95 | 5 | 12 | 5 | 12 | 70 | 40 | 4.8887e-07 | 3.5478 | -5.8581e-09 | 6.801e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | 2.1617e-05 | -0.0014557 | 4.8887e-07 | 3.6613e-09 | 1 | 0
1918 | 31.9667 | 5 | 12 | 5 | 12 | 70 | 40 | 4.824e-07 | 3.5478 | -6.4668e-09 | 6.711e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | 2.3375e-05 | -0.0014324 | 4.824e-07 | 4.0417e-09 | 1 | 0
1919 | 31.9833 | 5 | 12 | 5 | 12 | 70.0001 | 40 | 4.7535e-07 | 3.5478 | -7.0585e-09 | 6.6128e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 2.5078e-05 | -0.0014073 | 4.7535e-07 | 4.4116e-09 | 1 | 0
1920 | 32 | 5 | 12 | 5 | 12 | 70.0001 | 40 | 4.6771e-07 | 3.5478 | -7.6327e-09 | 6.5066e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 2.6724e-05 | -0.0013806 | 4.6771e-07 | 4.7705e-09 | 1 | 0
1921 | 32.0167 | 5 | 12 | 5 | 12 | 70.0001 | 40 | 4.5952e-07 | 3.5478 | -8.1888e-09 | 6.3927e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 2.8311e-05 | -0.0013523 | 4.5952e-07 | 5.118e-09 | 1 | 0
1922 | 32.0333 | 5 | 12 | 5 | 12 | 70.0001 | 40 | 4.508e-07 | 3.5478 | -8.7261e-09 | 6.2713e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 2.9837e-05 | -0.0013224 | 4.508e-07 | 5.4538e-09 | 1 | 0
1923 | 32.05 | 5 | 12 | 5 | 12 | 70.0001 | 40 | 4.4155e-07 | 3.5478 | -9.2443e-09 | 6.1427e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 3.1302e-05 | -0.0012911 | 4.4155e-07 | 5.7777e-09 | 1 | 0
1924 | 32.0667 | 5 | 12 | 5 | 12 | 70.0001 | 40 | 4.3181e-07 | 3.5478 | -9.7428e-09 | 6.0072e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 3.2704e-05 | -0.0012584 | 4.3181e-07 | 6.0892e-09 | 1 | 0
1925 | 32.0833 | 5 | 12 | 5 | 12 | 70.0001 | 40 | 4.2159e-07 | 3.5478 | -1.0221e-08 | 5.865e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 3.4042e-05 | -0.0012244 | 4.2159e-07 | 6.3882e-09 | 1 | 0
1926 | 32.1 | 5 | 12 | 5 | 12 | 70.0001 | 40 | 4.1091e-07 | 3.5478 | -1.0679e-08 | 5.7164e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 3.5315e-05 | -0.0011891 | 4.1091e-07 | 6.6743e-09 | 1 | 0
1927 | 32.1167 | 5 | 12 | 5 | 12 | 70.0001 | 40 | 3.998e-07 | 3.5478 | -1.1116e-08 | 5.5618e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 3.6523e-05 | -0.0011525 | 3.998e-07 | 6.9474e-09 | 1 | 0
1928 | 32.1333 | 5 | 12 | 5 | 12 | 70.0001 | 40 | 3.8826e-07 | 3.5478 | -1.1532e-08 | 5.4014e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 3.7663e-05 | -0.0011149 | 3.8826e-07 | 7.2072e-09 | 1 | 0
1929 | 32.15 | 5 | 12 | 5 | 12 | 70.0001 | 40 | 3.7634e-07 | 3.5478 | -1.1926e-08 | 5.2354e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 3.8735e-05 | -0.0010761 | 3.7634e-07 | 7.4536e-09 | 1 | 0
1930 | 32.1667 | 5 | 12 | 5 | 12 | 70.0001 | 40 | 3.6404e-07 | 3.5478 | -1.2298e-08 | 5.0644e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 3.974e-05 | -0.0010364 | 3.6404e-07 | 7.6863e-09 | 1 | 0
1931 | 32.1833 | 5 | 12 | 5 | 12 | 70.0001 | 40 | 3.5139e-07 | 3.5478 | -1.2648e-08 | 4.8884e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 4.0676e-05 | -0.00099572 | 3.5139e-07 | 7.9052e-09 | 1 | 0
1932 | 32.2 | 5 | 12 | 5 | 12 | 70.0001 | 40 | 3.3842e-07 | 3.5478 | -1.2976e-08 | 4.7079e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 4.1542e-05 | -0.00095418 | 3.3842e-07 | 8.1102e-09 | 1 | 0
1933 | 32.2167 | 5 | 12 | 5 | 12 | 70.0001 | 40 | 3.2513e-07 | 3.5478 | -1.3282e-08 | 4.5231e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 4.234e-05 | -0.00091184 | 3.2513e-07 | 8.3012e-09 | 1 | 0
1934 | 32.2333 | 5 | 12 | 5 | 12 | 70.0001 | 40 | 3.1157e-07 | 3.5478 | -1.3565e-08 | 4.3344e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 4.3067e-05 | -0.00086877 | 3.1157e-07 | 8.478e-09 | 1 | 0
1935 | 32.25 | 5 | 12 | 5 | 12 | 70.0001 | 40 | 2.9774e-07 | 3.5478 | -1.3825e-08 | 4.1421e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 4.3725e-05 | -0.00082505 | 2.9774e-07 | 8.6407e-09 | 1 | 0
1936 | 32.2667 | 5 | 12 | 5 | 12 | 70.0001 | 40 | 2.8368e-07 | 3.5478 | -1.4063e-08 | 3.9464e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 4.4313e-05 | -0.00078073 | 2.8368e-07 | 8.7892e-09 | 1 | 0
1937 | 32.2833 | 5 | 12 | 5 | 12 | 70.0001 | 40 | 2.694e-07 | 3.5478 | -1.4278e-08 | 3.7478e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 4.4831e-05 | -0.0007359 | 2.694e-07 | 8.9235e-09 | 1 | 0
1938 | 32.3 | 5 | 12 | 5 | 12 | 70.0001 | 40 | 2.5493e-07 | 3.5478 | -1.447e-08 | 3.5465e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 4.528e-05 | -0.00069062 | 2.5493e-07 | 9.0435e-09 | 1 | 0
1939 | 32.3167 | 5 | 12 | 5 | 12 | 70.0001 | 40 | 2.4029e-07 | 3.5478 | -1.4639e-08 | 3.3429e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 4.566e-05 | -0.00064496 | 2.4029e-07 | 9.1493e-09 | 1 | 0
1940 | 32.3333 | 5 | 12 | 5 | 12 | 70.0001 | 40 | 2.2551e-07 | 3.5478 | -1.4785e-08 | 3.1372e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 4.597e-05 | -0.00059899 | 2.2551e-07 | 9.2409e-09 | 1 | 0
1941 | 32.35 | 5 | 12 | 5 | 12 | 70.0001 | 40 | 2.106e-07 | 3.5478 | -1.4909e-08 | 2.9298e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 4.6213e-05 | -0.00055278 | 2.106e-07 | 9.3183e-09 | 1 | 0
1942 | 32.3667 | 5 | 12 | 5 | 12 | 70.0001 | 40 | 1.9559e-07 | 3.5478 | -1.5011e-08 | 2.721e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 4.6387e-05 | -0.00050639 | 1.9559e-07 | 9.3817e-09 | 1 | 0
1943 | 32.3833 | 5 | 12 | 5 | 12 | 70.0001 | 40 | 1.805e-07 | 3.5478 | -1.509e-08 | 2.511e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 4.6494e-05 | -0.0004599 | 1.805e-07 | 9.4311e-09 | 1 | 0
1944 | 32.4 | 5 | 12 | 5 | 12 | 70.0001 | 40 | 1.6535e-07 | 3.5478 | -1.5147e-08 | 2.3003e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 4.6535e-05 | -0.00041336 | 1.6535e-07 | 9.4667e-09 | 1 | 0
1945 | 32.4167 | 5 | 12 | 5 | 12 | 70.0001 | 40 | 1.5017e-07 | 3.5478 | -1.5182e-08 | 2.0891e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 4.651e-05 | -0.00036685 | 1.5017e-07 | 9.4886e-09 | 1 | 0
1946 | 32.4333 | 5 | 12 | 5 | 12 | 70.0001 | 40 | 1.3498e-07 | 3.5478 | -1.5195e-08 | 1.8777e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 4.642e-05 | -0.00032043 | 1.3498e-07 | 9.4969e-09 | 1 | 0
1947 | 32.45 | 5 | 12 | 5 | 12 | 70.0001 | 40 | 1.1979e-07 | 3.5478 | -1.5187e-08 | 1.6665e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 4.6266e-05 | -0.00027417 | 1.1979e-07 | 9.4918e-09 | 1 | 0
1948 | 32.4667 | 5 | 12 | 5 | 12 | 70.0001 | 40 | 1.0463e-07 | 3.5478 | -1.5157e-08 | 1.4556e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 4.6049e-05 | -0.00022812 | 1.0463e-07 | 9.4734e-09 | 1 | 0
1949 | 32.4833 | 5 | 12 | 5 | 12 | 70.0001 | 40 | 8.9524e-08 | 3.5478 | -1.5107e-08 | 1.2454e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 4.5771e-05 | -0.00018235 | 8.9524e-08 | 9.442e-09 | 1 | 0
1950 | 32.5 | 5 | 12 | 5 | 12 | 70.0001 | 40 | 7.4488e-08 | 3.5478 | -1.5037e-08 | 1.0362e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 4.5432e-05 | -0.00013692 | 7.4488e-08 | 9.3978e-09 | 1 | 0
1951 | 32.5167 | 5 | 12 | 5 | 12 | 70.0001 | 40 | 5.9542e-08 | 3.5478 | -1.4946e-08 | 8.2832e-07 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 4.5034e-05 | -9.1881e-05 | 5.9542e-08 | 9.341e-09 | 1 | 0
1952 | 32.5333 | 5 | 12 | 5 | 12 | 70.0001 | 40 | 4.4707e-08 | 3.5478 | -1.4835e-08 | 6.2194e-07 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 4.4578e-05 | -4.7302e-05 | 4.4707e-08 | 9.2719e-09 | 1 | 0
1953 | 32.55 | 5 | 12 | 5 | 12 | 70.0001 | 40 | 3.0002e-08 | 3.5478 | -1.4705e-08 | 4.1737e-07 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 4.4066e-05 | -3.2363e-06 | 3.0002e-08 | 9.1907e-09 | 1 | 0
1954 | 32.5667 | 5 | 12 | 5 | 12 | 70.0001 | 40 | 1.5446e-08 | 3.5478 | -1.4556e-08 | 2.1487e-07 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 4.3499e-05 | 4.0262e-05 | 1.5446e-08 | 9.0976e-09 | 1 | 0
1955 | 32.5833 | 5 | 12 | 5 | 12 | 70.0001 | 40 | 1.0568e-09 | 3.5478 | -1.4389e-08 | 1.4701e-08 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 4.2877e-05 | 8.314e-05 | 1.0568e-09 | 8.9931e-09 | 1 | 0
1956 | 32.6 | 5 | 12 | 5 | 12 | 70.0001 | 40 | -1.3147e-08 | 3.5478 | -1.4204e-08 | -1.8289e-07 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 4.2204e-05 | 0.00012534 | 1.3147e-08 | 8.8772e-09 | 1 | 0
1957 | 32.6167 | 5 | 12 | 5 | 12 | 70.0001 | 40 | -2.7148e-08 | 3.5478 | -1.4001e-08 | -3.7767e-07 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 4.1481e-05 | 0.00016682 | 2.7148e-08 | 8.7505e-09 | 1 | 0
1958 | 32.6333 | 5 | 12 | 5 | 12 | 70.0001 | 40 | -4.0929e-08 | 3.5478 | -1.3781e-08 | -5.6938e-07 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 4.0709e-05 | 0.00020753 | 4.0929e-08 | 8.6131e-09 | 1 | 0
1959 | 32.65 | 5 | 12 | 5 | 12 | 70.0001 | 40 | -5.4473e-08 | 3.5478 | -1.3545e-08 | -7.5781e-07 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 3.989e-05 | 0.00024742 | 5.4473e-08 | 8.4655e-09 | 1 | 0
1960 | 32.6667 | 5 | 12 | 5 | 12 | 70.0001 | 40 | -6.7766e-08 | 3.5478 | -1.3293e-08 | -9.4273e-07 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 3.9025e-05 | 0.00028645 | 6.7766e-08 | 8.3079e-09 | 1 | 0
1961 | 32.6833 | 5 | 12 | 5 | 12 | 70.0001 | 40 | -8.0791e-08 | 3.5478 | -1.3025e-08 | -1.1239e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 3.8117e-05 | 0.00032457 | 8.0791e-08 | 8.1407e-09 | 1 | 0
1962 | 32.7 | 5 | 12 | 5 | 12 | 70.0001 | 40 | -9.3534e-08 | 3.5478 | -1.2743e-08 | -1.3012e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 3.7168e-05 | 0.00036173 | 9.3534e-08 | 7.9643e-09 | 1 | 0
1963 | 32.7167 | 5 | 12 | 5 | 12 | 70.0001 | 40 | -1.0598e-07 | 3.5478 | -1.2446e-08 | -1.4744e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 3.6179e-05 | 0.00039791 | 1.0598e-07 | 7.7791e-09 | 1 | 0
1964 | 32.7333 | 5 | 12 | 5 | 12 | 70.0001 | 40 | -1.1812e-07 | 3.5478 | -1.2136e-08 | -1.6432e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 3.5152e-05 | 0.00043306 | 1.1812e-07 | 7.5853e-09 | 1 | 0
1965 | 32.75 | 5 | 12 | 5 | 12 | 70.0001 | 40 | -1.2993e-07 | 3.5478 | -1.1813e-08 | -1.8075e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 3.4089e-05 | 0.00046715 | 1.2993e-07 | 7.3834e-09 | 1 | 0
1966 | 32.7667 | 5 | 12 | 5 | 12 | 70.0001 | 40 | -1.4141e-07 | 3.5478 | -1.1478e-08 | -1.9672e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 3.2992e-05 | 0.00050015 | 1.4141e-07 | 7.1738e-09 | 1 | 0
1967 | 32.7833 | 5 | 12 | 5 | 12 | 70.0001 | 40 | -1.5254e-07 | 3.5478 | -1.1131e-08 | -2.1221e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 3.1863e-05 | 0.00053201 | 1.5254e-07 | 6.9569e-09 | 1 | 0
1968 | 32.8 | 5 | 12 | 5 | 12 | 70.0001 | 40 | -1.6331e-07 | 3.5478 | -1.0773e-08 | -2.2719e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 3.0704e-05 | 0.00056271 | 1.6331e-07 | 6.7331e-09 | 1 | 0
1969 | 32.8167 | 5 | 12 | 5 | 12 | 70.0001 | 40 | -1.7372e-07 | 3.5478 | -1.0404e-08 | -2.4167e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 2.9518e-05 | 0.00059223 | 1.7372e-07 | 6.5027e-09 | 1 | 0
1970 | 32.8333 | 5 | 12 | 5 | 12 | 70.0001 | 40 | -1.8374e-07 | 3.5478 | -1.0026e-08 | -2.5562e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 2.8305e-05 | 0.00062054 | 1.8374e-07 | 6.2662e-09 | 1 | 0
1971 | 32.85 | 5 | 12 | 5 | 12 | 70.0001 | 40 | -1.9338e-07 | 3.5478 | -9.6384e-09 | -2.6902e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 2.7068e-05 | 0.0006476 | 1.9338e-07 | 6.024e-09 | 1 | 0
1972 | 32.8667 | 5 | 12 | 5 | 12 | 70.0001 | 40 | -2.0262e-07 | 3.5478 | -9.2424e-09 | -2.8188e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70.0001 | 35 | 15 | 35 | 2.581e-05 | 0.00067341 | 2.0262e-07 | 5.7765e-09 | 1 | 0
1973 | 32.8833 | 5 | 12 | 5 | 12 | 70 | 40 | -2.1146e-07 | 3.5478 | -8.8386e-09 | -2.9418e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | 2.4531e-05 | 0.00069794 | 2.1146e-07 | 5.5241e-09 | 1 | 0
1974 | 32.9 | 5 | 12 | 5 | 12 | 70 | 40 | -2.1989e-07 | 3.5478 | -8.4277e-09 | -3.059e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | 2.3235e-05 | 0.00072118 | 2.1989e-07 | 5.2673e-09 | 1 | 0
1975 | 32.9167 | 5 | 12 | 5 | 12 | 70 | 40 | -2.279e-07 | 3.5478 | -8.0103e-09 | -3.1704e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | 2.1924e-05 | 0.0007431 | 2.279e-07 | 5.0064e-09 | 1 | 0
1976 | 32.9333 | 5 | 12 | 5 | 12 | 70 | 40 | -2.3549e-07 | 3.5478 | -7.5871e-09 | -3.276e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | 2.0598e-05 | 0.0007637 | 2.3549e-07 | 4.7419e-09 | 1 | 0
1977 | 32.95 | 5 | 12 | 5 | 12 | 70 | 40 | -2.4265e-07 | 3.5478 | -7.1587e-09 | -3.3756e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | 1.9261e-05 | 0.00078296 | 2.4265e-07 | 4.4742e-09 | 1 | 0
1978 | 32.9667 | 5 | 12 | 5 | 12 | 70 | 40 | -2.4937e-07 | 3.5478 | -6.7259e-09 | -3.4692e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | 1.7914e-05 | 0.00080088 | 2.4937e-07 | 4.2037e-09 | 1 | 0
1979 | 32.9833 | 5 | 12 | 5 | 12 | 70 | 40 | -2.5566e-07 | 3.5478 | -6.2893e-09 | -3.5566e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | 1.656e-05 | 0.00081744 | 2.5566e-07 | 3.9308e-09 | 1 | 0
1980 | 33 | 5 | 12 | 5 | 12 | 70 | 40 | -2.6151e-07 | 3.5478 | -5.8496e-09 | -3.638e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | 1.52e-05 | 0.00083264 | 2.6151e-07 | 3.656e-09 | 1 | 0
1981 | 33.0167 | 5 | 12 | 5 | 12 | 70 | 40 | -2.6692e-07 | 3.5478 | -5.4073e-09 | -3.7132e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | 1.3836e-05 | 0.00084647 | 2.6692e-07 | 3.3796e-09 | 1 | 0
1982 | 33.0333 | 5 | 12 | 5 | 12 | 70 | 40 | -2.7188e-07 | 3.5478 | -4.9633e-09 | -3.7823e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | 1.2471e-05 | 0.00085894 | 2.7188e-07 | 3.102e-09 | 1 | 0
1983 | 33.05 | 5 | 12 | 5 | 12 | 70 | 40 | -2.764e-07 | 3.5478 | -4.518e-09 | -3.8451e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | 1.1106e-05 | 0.00087005 | 2.764e-07 | 2.8238e-09 | 1 | 0
1984 | 33.0667 | 5 | 12 | 5 | 12 | 70 | 40 | -2.8047e-07 | 3.5478 | -4.0722e-09 | -3.9018e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | 9.7433e-06 | 0.00087979 | 2.8047e-07 | 2.5451e-09 | 1 | 0
1985 | 33.0833 | 5 | 12 | 5 | 12 | 70 | 40 | -2.841e-07 | 3.5478 | -3.6265e-09 | -3.9522e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | 8.3845e-06 | 0.00088818 | 2.841e-07 | 2.2666e-09 | 1 | 0
1986 | 33.1 | 5 | 12 | 5 | 12 | 70 | 40 | -2.8728e-07 | 3.5478 | -3.1815e-09 | -3.9965e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | 7.0316e-06 | 0.00089521 | 2.8728e-07 | 1.9884e-09 | 1 | 0
1987 | 33.1167 | 5 | 12 | 5 | 12 | 70 | 40 | -2.9002e-07 | 3.5478 | -2.7378e-09 | -4.0346e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | 5.6864e-06 | 0.0009009 | 2.9002e-07 | 1.7111e-09 | 1 | 0
1988 | 33.1333 | 5 | 12 | 5 | 12 | 70 | 40 | -2.9231e-07 | 3.5478 | -2.296e-09 | -4.0665e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | 4.3507e-06 | 0.00090525 | 2.9231e-07 | 1.435e-09 | 1 | 0
1989 | 33.15 | 5 | 12 | 5 | 12 | 70 | 40 | -2.9417e-07 | 3.5478 | -1.8568e-09 | -4.0924e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | 3.0262e-06 | 0.00090827 | 2.9417e-07 | 1.1605e-09 | 1 | 0
1990 | 33.1667 | 5 | 12 | 5 | 12 | 70 | 40 | -2.9559e-07 | 3.5478 | -1.4206e-09 | -4.1121e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | 1.7147e-06 | 0.00090999 | 2.9559e-07 | 8.8789e-10 | 1 | 0
1991 | 33.1833 | 5 | 12 | 5 | 12 | 70 | 40 | -2.9658e-07 | 3.5478 | -9.8815e-10 | -4.1259e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | 4.1783e-07 | 0.00091041 | 2.9658e-07 | 6.1759e-10 | 1 | 0
1992 | 33.2 | 5 | 12 | 5 | 12 | 70 | 40 | -2.9714e-07 | 3.5478 | -5.599e-10 | -4.1337e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -8.628e-07 | 0.00090954 | 2.9714e-07 | 3.4994e-10 | 1 | 0
1993 | 33.2167 | 5 | 12 | 5 | 12 | 70 | 40 | -2.9728e-07 | 3.5478 | -1.3643e-10 | -4.1356e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -2.1256e-06 | 0.00090742 | 2.9728e-07 | 8.527e-11 | 1 | 0
1994 | 33.2333 | 5 | 12 | 5 | 12 | 70 | 40 | -2.9699e-07 | 3.5478 | 2.8173e-10 | -4.1316e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -3.369e-06 | 0.00090405 | 2.9699e-07 | -1.7608e-10 | -1 | -2
1995 | 33.25 | 5 | 12 | 5 | 12 | 70 | 40 | -2.963e-07 | 3.5478 | 6.9407e-10 | -4.122e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -4.5916e-06 | 0.00089946 | 2.963e-07 | -4.338e-10 | -1 | 0
1996 | 33.2667 | 5 | 12 | 5 | 12 | 70 | 40 | -2.952e-07 | 3.5478 | 1.1001e-09 | -4.1067e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -5.7918e-06 | 0.00089367 | 2.952e-07 | -6.8755e-10 | -1 | 0
1997 | 33.2833 | 5 | 12 | 5 | 12 | 70 | 40 | -2.937e-07 | 3.5478 | 1.4993e-09 | -4.0858e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -6.9684e-06 | 0.0008867 | 2.937e-07 | -9.3706e-10 | -1 | 0
1998 | 33.3 | 5 | 12 | 5 | 12 | 70 | 40 | -2.9181e-07 | 3.5478 | 1.8912e-09 | -4.0595e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -8.1199e-06 | 0.00087858 | 2.9181e-07 | -1.182e-09 | -1 | 0
1999 | 33.3167 | 5 | 12 | 5 | 12 | 70 | 40 | -2.8953e-07 | 3.5478 | 2.2754e-09 | -4.0279e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -9.2452e-06 | 0.00086933 | 2.8953e-07 | -1.4221e-09 | -1 | 0
2000 | 33.3333 | 5 | 12 | 5 | 12 | 70 | 40 | -2.8688e-07 | 3.5478 | 2.6514e-09 | -3.991e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -1.0343e-05 | 0.00085899 | 2.8688e-07 | -1.6571e-09 | -1 | 0
2001 | 33.35 | 5 | 12 | 5 | 12 | 70 | 40 | -2.8386e-07 | 3.5478 | 3.0188e-09 | -3.949e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -1.1412e-05 | 0.00084758 | 2.8386e-07 | -1.8868e-09 | -1 | 0
2002 | 33.3667 | 5 | 12 | 5 | 12 | 70 | 40 | -2.8049e-07 | 3.5478 | 3.3772e-09 | -3.902e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -1.2451e-05 | 0.00083513 | 2.8049e-07 | -2.1108e-09 | -1 | 0
2003 | 33.3833 | 5 | 12 | 5 | 12 | 70 | 40 | -2.7676e-07 | 3.5478 | 3.7263e-09 | -3.8502e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -1.3459e-05 | 0.00082167 | 2.7676e-07 | -2.3289e-09 | -1 | 0
2004 | 33.4 | 5 | 12 | 5 | 12 | 70 | 40 | -2.7269e-07 | 3.5478 | 4.0656e-09 | -3.7936e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -1.4435e-05 | 0.00080723 | 2.7269e-07 | -2.541e-09 | -1 | 0
2005 | 33.4167 | 5 | 12 | 5 | 12 | 70 | 40 | -2.683e-07 | 3.5478 | 4.3947e-09 | -3.7325e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -1.5378e-05 | 0.00079185 | 2.683e-07 | -2.7467e-09 | -1 | 0
2006 | 33.4333 | 5 | 12 | 5 | 12 | 70 | 40 | -2.6359e-07 | 3.5478 | 4.7135e-09 | -3.6669e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -1.6288e-05 | 0.00077557 | 2.6359e-07 | -2.9459e-09 | -1 | 0
2007 | 33.45 | 5 | 12 | 5 | 12 | 70 | 40 | -2.5856e-07 | 3.5478 | 5.0215e-09 | -3.597e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -1.7163e-05 | 0.0007584 | 2.5856e-07 | -3.1385e-09 | -1 | 0
2008 | 33.4667 | 5 | 12 | 5 | 12 | 70 | 40 | -2.5325e-07 | 3.5478 | 5.3185e-09 | -3.523e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -1.8002e-05 | 0.0007404 | 2.5325e-07 | -3.3241e-09 | -1 | 0
2009 | 33.4833 | 5 | 12 | 5 | 12 | 70 | 40 | -2.4764e-07 | 3.5478 | 5.6042e-09 | -3.4451e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -1.8806e-05 | 0.0007216 | 2.4764e-07 | -3.5026e-09 | -1 | 0
2010 | 33.5 | 5 | 12 | 5 | 12 | 70 | 40 | -2.4176e-07 | 3.5478 | 5.8783e-09 | -3.3633e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -1.9572e-05 | 0.00070202 | 2.4176e-07 | -3.6739e-09 | -1 | 0
2011 | 33.5167 | 5 | 12 | 5 | 12 | 70 | 40 | -2.3562e-07 | 3.5478 | 6.1406e-09 | -3.2779e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -2.0302e-05 | 0.00068172 | 2.3562e-07 | -3.8379e-09 | -1 | 0
2012 | 33.5333 | 5 | 12 | 5 | 12 | 70 | 40 | -2.2923e-07 | 3.5478 | 6.391e-09 | -3.189e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -2.0993e-05 | 0.00066073 | 2.2923e-07 | -3.9943e-09 | -1 | 0
2013 | 33.55 | 5 | 12 | 5 | 12 | 70 | 40 | -2.226e-07 | 3.5478 | 6.6291e-09 | -3.0968e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -2.1646e-05 | 0.00063908 | 2.226e-07 | -4.1432e-09 | -1 | 0
2014 | 33.5667 | 5 | 12 | 5 | 12 | 70 | 40 | -2.1575e-07 | 3.5478 | 6.8548e-09 | -3.0014e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -2.226e-05 | 0.00061682 | 2.1575e-07 | -4.2843e-09 | -1 | 0
2015 | 33.5833 | 5 | 12 | 5 | 12 | 70 | 40 | -2.0868e-07 | 3.5478 | 7.068e-09 | -2.9031e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -2.2835e-05 | 0.00059399 | 2.0868e-07 | -4.4175e-09 | -1 | 0
2016 | 33.6 | 5 | 12 | 5 | 12 | 70 | 40 | -2.0141e-07 | 3.5478 | 7.2686e-09 | -2.8019e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -2.3371e-05 | 0.00057062 | 2.0141e-07 | -4.5429e-09 | -1 | 0
2017 | 33.6167 | 5 | 12 | 5 | 12 | 70 | 40 | -1.9396e-07 | 3.5478 | 7.4563e-09 | -2.6982e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -2.3866e-05 | 0.00054675 | 1.9396e-07 | -4.6602e-09 | -1 | 0
2018 | 33.6333 | 5 | 12 | 5 | 12 | 70 | 40 | -1.8632e-07 | 3.5478 | 7.6312e-09 | -2.5921e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -2.4322e-05 | 0.00052243 | 1.8632e-07 | -4.7695e-09 | -1 | 0
2019 | 33.65 | 5 | 12 | 5 | 12 | 70 | 40 | -1.7853e-07 | 3.5478 | 7.7931e-09 | -2.4836e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -2.4739e-05 | 0.00049769 | 1.7853e-07 | -4.8707e-09 | -1 | 0
2020 | 33.6667 | 5 | 12 | 5 | 12 | 69.9999 | 40 | -1.7059e-07 | 3.5478 | 7.942e-09 | -2.3732e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 35 | 15 | 35 | -2.5114e-05 | 0.00047258 | 1.7059e-07 | -4.9638e-09 | -1 | 0
2021 | 33.6833 | 5 | 12 | 5 | 12 | 69.9999 | 40 | -1.6251e-07 | 3.5478 | 8.0779e-09 | -2.2608e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 35 | 15 | 35 | -2.545e-05 | 0.00044712 | 1.6251e-07 | -5.0487e-09 | -1 | 0
2022 | 33.7 | 5 | 12 | 5 | 12 | 69.9999 | 40 | -1.5431e-07 | 3.5478 | 8.2006e-09 | -2.1467e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 35 | 15 | 35 | -2.5746e-05 | 0.00042138 | 1.5431e-07 | -5.1254e-09 | -1 | 0
2023 | 33.7167 | 5 | 12 | 5 | 12 | 69.9999 | 40 | -1.46e-07 | 3.5478 | 8.3103e-09 | -2.0311e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 35 | 15 | 35 | -2.6002e-05 | 0.00039538 | 1.46e-07 | -5.194e-09 | -1 | 0
2024 | 33.7333 | 5 | 12 | 5 | 12 | 69.9999 | 40 | -1.3759e-07 | 3.5478 | 8.407e-09 | -1.9141e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 35 | 15 | 35 | -2.6219e-05 | 0.00036916 | 1.3759e-07 | -5.2543e-09 | -1 | 0
2025 | 33.75 | 5 | 12 | 5 | 12 | 69.9999 | 40 | -1.291e-07 | 3.5478 | 8.4905e-09 | -1.796e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 35 | 15 | 35 | -2.6395e-05 | 0.00034276 | 1.291e-07 | -5.3066e-09 | -1 | 0
2026 | 33.7667 | 5 | 12 | 5 | 12 | 69.9999 | 40 | -1.2054e-07 | 3.5478 | 8.5612e-09 | -1.6769e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 35 | 15 | 35 | -2.6533e-05 | 0.00031623 | 1.2054e-07 | -5.3507e-09 | -1 | 0
2027 | 33.7833 | 5 | 12 | 5 | 12 | 69.9999 | 40 | -1.1192e-07 | 3.5478 | 8.6189e-09 | -1.557e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 35 | 15 | 35 | -2.6631e-05 | 0.0002896 | 1.1192e-07 | -5.3868e-09 | -1 | 0
2028 | 33.8 | 5 | 12 | 5 | 12 | 69.9999 | 40 | -1.0326e-07 | 3.5478 | 8.6637e-09 | -1.4365e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 35 | 15 | 35 | -2.6691e-05 | 0.00026291 | 1.0326e-07 | -5.4148e-09 | -1 | 0
2029 | 33.8167 | 5 | 12 | 5 | 12 | 69.9999 | 40 | -9.4563e-08 | 3.5478 | 8.6959e-09 | -1.3155e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 35 | 15 | 35 | -2.6713e-05 | 0.00023619 | 9.4563e-08 | -5.4349e-09 | -1 | 0
2030 | 33.8333 | 5 | 12 | 5 | 12 | 69.9999 | 40 | -8.5847e-08 | 3.5478 | 8.7155e-09 | -1.1943e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 35 | 15 | 35 | -2.6697e-05 | 0.0002095 | 8.5847e-08 | -5.4472e-09 | -1 | 0
2031 | 33.85 | 5 | 12 | 5 | 12 | 69.9999 | 40 | -7.7125e-08 | 3.5478 | 8.7226e-09 | -1.0729e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 35 | 15 | 35 | -2.6644e-05 | 0.00018285 | 7.7125e-08 | -5.4516e-09 | -1 | 0
2032 | 33.8667 | 5 | 12 | 5 | 12 | 69.9999 | 40 | -6.8407e-08 | 3.5478 | 8.7174e-09 | -9.5165e-07 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 35 | 15 | 35 | -2.6554e-05 | 0.0001563 | 6.8407e-08 | -5.4484e-09 | -1 | 0
2033 | 33.8833 | 5 | 12 | 5 | 12 | 69.9999 | 40 | -5.9707e-08 | 3.5478 | 8.7e-09 | -8.3062e-07 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 35 | 15 | 35 | -2.6428e-05 | 0.00012987 | 5.9707e-08 | -5.4375e-09 | -1 | 0
2034 | 33.9 | 5 | 12 | 5 | 12 | 69.9999 | 40 | -5.1037e-08 | 3.5478 | 8.6707e-09 | -7.1e-07 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 35 | 15 | 35 | -2.6267e-05 | 0.0001036 | 5.1037e-08 | -5.4192e-09 | -1 | 0
2035 | 33.9167 | 5 | 12 | 5 | 12 | 69.9999 | 40 | -4.2407e-08 | 3.5478 | 8.6297e-09 | -5.8995e-07 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 35 | 15 | 35 | -2.6071e-05 | 7.7533e-05 | 4.2407e-08 | -5.3935e-09 | -1 | 0
2036 | 33.9333 | 5 | 12 | 5 | 12 | 69.9999 | 40 | -3.383e-08 | 3.5478 | 8.577e-09 | -4.7063e-07 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 35 | 15 | 35 | -2.5841e-05 | 5.1691e-05 | 3.383e-08 | -5.3606e-09 | -1 | 0
2037 | 33.95 | 5 | 12 | 5 | 12 | 69.9999 | 40 | -2.5317e-08 | 3.5478 | 8.5131e-09 | -3.522e-07 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 35 | 15 | 35 | -2.5578e-05 | 2.6113e-05 | 2.5317e-08 | -5.3207e-09 | -1 | 0
2038 | 33.9667 | 5 | 12 | 5 | 12 | 69.9999 | 40 | -1.6879e-08 | 3.5478 | 8.438e-09 | -2.3481e-07 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 69.9999 | 35 | 15 | 35 | -2.5283e-05 | 8.2984e-07 | 1.6879e-08 | -5.2738e-09 | -1 | 0
2039 | 33.9833 | 5 | 12 | 5 | 12 | 70 | 40 | -8.5266e-09 | 3.5478 | 8.3521e-09 | -1.1862e-07 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -2.4956e-05 | -2.4126e-05 | 8.5266e-09 | -5.2201e-09 | -1 | 0
2040 | 34 | 5 | 12 | 5 | 12 | 70 | 40 | -2.7097e-10 | 3.5478 | 8.2556e-09 | -3.7696e-09 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -2.4598e-05 | -4.8724e-05 | 2.7097e-10 | -5.1598e-09 | -1 | 0
2041 | 34.0167 | 5 | 12 | 5 | 12 | 70 | 40 | 7.8779e-09 | 3.5478 | 8.1489e-09 | 1.0959e-07 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -2.4211e-05 | -7.2935e-05 | 7.8779e-09 | -5.093e-09 | -1 | 0
2042 | 34.0333 | 5 | 12 | 5 | 12 | 70 | 40 | 1.591e-08 | 3.5478 | 8.032e-09 | 2.2133e-07 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -2.3794e-05 | -9.6729e-05 | 1.591e-08 | -5.02e-09 | -1 | 0
2043 | 34.05 | 5 | 12 | 5 | 12 | 70 | 40 | 2.3815e-08 | 3.5478 | 7.9055e-09 | 3.3131e-07 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -2.335e-05 | -0.00012008 | 2.3815e-08 | -4.9409e-09 | -1 | 0
2044 | 34.0667 | 5 | 12 | 5 | 12 | 70 | 40 | 3.1585e-08 | 3.5478 | 7.7695e-09 | 4.394e-07 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -2.2878e-05 | -0.00014296 | 3.1585e-08 | -4.8559e-09 | -1 | 0
2045 | 34.0833 | 5 | 12 | 5 | 12 | 70 | 40 | 3.9209e-08 | 3.5478 | 7.6244e-09 | 5.4546e-07 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -2.2381e-05 | -0.00016534 | 3.9209e-08 | -4.7653e-09 | -1 | 0
2046 | 34.1 | 5 | 12 | 5 | 12 | 70 | 40 | 4.668e-08 | 3.5478 | 7.4705e-09 | 6.4939e-07 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -2.1859e-05 | -0.0001872 | 4.668e-08 | -4.6691e-09 | -1 | 0
2047 | 34.1167 | 5 | 12 | 5 | 12 | 70 | 40 | 5.3988e-08 | 3.5478 | 7.3081e-09 | 7.5106e-07 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -2.1313e-05 | -0.00020851 | 5.3988e-08 | -4.5676e-09 | -1 | 0
2048 | 34.1333 | 5 | 12 | 5 | 12 | 70 | 40 | 6.1126e-08 | 3.5478 | 7.1377e-09 | 8.5035e-07 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -2.0744e-05 | -0.00022925 | 6.1126e-08 | -4.461e-09 | -1 | 0
2049 | 34.15 | 5 | 12 | 5 | 12 | 70 | 40 | 6.8085e-08 | 3.5478 | 6.9594e-09 | 9.4717e-07 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -2.0154e-05 | -0.00024941 | 6.8085e-08 | -4.3496e-09 | -1 | 0
2050 | 34.1667 | 5 | 12 | 5 | 12 | 70 | 40 | 7.4859e-08 | 3.5478 | 6.7737e-09 | 1.0414e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -1.9543e-05 | -0.00026895 | 7.4859e-08 | -4.2335e-09 | -1 | 0
2051 | 34.1833 | 5 | 12 | 5 | 12 | 70 | 40 | 8.144e-08 | 3.5478 | 6.5809e-09 | 1.133e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -1.8913e-05 | -0.00028786 | 8.144e-08 | -4.113e-09 | -1 | 0
2052 | 34.2 | 5 | 12 | 5 | 12 | 70 | 40 | 8.7821e-08 | 3.5478 | 6.3814e-09 | 1.2217e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -1.8264e-05 | -0.00030613 | 8.7821e-08 | -3.9884e-09 | -1 | 0
2053 | 34.2167 | 5 | 12 | 5 | 12 | 70 | 40 | 9.3996e-08 | 3.5478 | 6.1755e-09 | 1.3076e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -1.7598e-05 | -0.00032373 | 9.3996e-08 | -3.8597e-09 | -1 | 0
2054 | 34.2333 | 5 | 12 | 5 | 12 | 70 | 40 | 9.996e-08 | 3.5478 | 5.9637e-09 | 1.3906e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -1.6916e-05 | -0.00034064 | 9.996e-08 | -3.7273e-09 | -1 | 0
2055 | 34.25 | 5 | 12 | 5 | 12 | 70 | 40 | 1.0571e-07 | 3.5478 | 5.7463e-09 | 1.4705e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -1.6219e-05 | -0.00035686 | 1.0571e-07 | -3.5914e-09 | -1 | 0
2056 | 34.2667 | 5 | 12 | 5 | 12 | 70 | 40 | 1.1123e-07 | 3.5478 | 5.5236e-09 | 1.5474e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -1.5509e-05 | -0.00037237 | 1.1123e-07 | -3.4523e-09 | -1 | 0
2057 | 34.2833 | 5 | 12 | 5 | 12 | 70 | 40 | 1.1653e-07 | 3.5478 | 5.2961e-09 | 1.6211e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -1.4786e-05 | -0.00038716 | 1.1653e-07 | -3.3101e-09 | -1 | 0
2058 | 34.3 | 5 | 12 | 5 | 12 | 70 | 40 | 1.2159e-07 | 3.5478 | 5.0641e-09 | 1.6915e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -1.4052e-05 | -0.00040121 | 1.2159e-07 | -3.1651e-09 | -1 | 0
2059 | 34.3167 | 5 | 12 | 5 | 12 | 70 | 40 | 1.2642e-07 | 3.5478 | 4.8281e-09 | 1.7587e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -1.3307e-05 | -0.00041452 | 1.2642e-07 | -3.0176e-09 | -1 | 0
2060 | 34.3333 | 5 | 12 | 5 | 12 | 70 | 40 | 1.3101e-07 | 3.5478 | 4.5883e-09 | 1.8225e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -1.2554e-05 | -0.00042707 | 1.3101e-07 | -2.8677e-09 | -1 | 0
2061 | 34.35 | 5 | 12 | 5 | 12 | 70 | 40 | 1.3535e-07 | 3.5478 | 4.3453e-09 | 1.883e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -1.1793e-05 | -0.00043886 | 1.3535e-07 | -2.7158e-09 | -1 | 0
2062 | 34.3667 | 5 | 12 | 5 | 12 | 70 | 40 | 1.3945e-07 | 3.5478 | 4.0993e-09 | 1.94e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -1.1025e-05 | -0.00044989 | 1.3945e-07 | -2.562e-09 | -1 | 0
2063 | 34.3833 | 5 | 12 | 5 | 12 | 70 | 40 | 1.433e-07 | 3.5478 | 3.8507e-09 | 1.9936e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -1.0252e-05 | -0.00046014 | 1.433e-07 | -2.4067e-09 | -1 | 0
2064 | 34.4 | 5 | 12 | 5 | 12 | 70 | 40 | 1.469e-07 | 3.5478 | 3.6e-09 | 2.0436e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -9.4742e-06 | -0.00046961 | 1.469e-07 | -2.25e-09 | -1 | 0
2065 | 34.4167 | 5 | 12 | 5 | 12 | 70 | 40 | 1.5025e-07 | 3.5478 | 3.3475e-09 | 2.0902e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -8.6934e-06 | -0.00047831 | 1.5025e-07 | -2.0922e-09 | -1 | 0
2066 | 34.4333 | 5 | 12 | 5 | 12 | 70 | 40 | 1.5334e-07 | 3.5478 | 3.0936e-09 | 2.1332e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -7.9106e-06 | -0.00048622 | 1.5334e-07 | -1.9335e-09 | -1 | 0
2067 | 34.45 | 5 | 12 | 5 | 12 | 70 | 40 | 1.5618e-07 | 3.5478 | 2.8387e-09 | 2.1727e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -7.1269e-06 | -0.00049334 | 1.5618e-07 | -1.7742e-09 | -1 | 0
2068 | 34.4667 | 5 | 12 | 5 | 12 | 70 | 40 | 1.5876e-07 | 3.5478 | 2.5831e-09 | 2.2087e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -6.3433e-06 | -0.00049969 | 1.5876e-07 | -1.6144e-09 | -1 | 0
2069 | 34.4833 | 5 | 12 | 5 | 12 | 70 | 40 | 1.6109e-07 | 3.5478 | 2.3271e-09 | 2.241e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -5.5611e-06 | -0.00050525 | 1.6109e-07 | -1.4545e-09 | -1 | 0
2070 | 34.5 | 5 | 12 | 5 | 12 | 70 | 40 | 1.6316e-07 | 3.5478 | 2.0713e-09 | 2.2699e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -4.7812e-06 | -0.00051003 | 1.6316e-07 | -1.2946e-09 | -1 | 0
2071 | 34.5167 | 5 | 12 | 5 | 12 | 70 | 40 | 1.6498e-07 | 3.5478 | 1.8159e-09 | 2.2951e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -4.0047e-06 | -0.00051403 | 1.6498e-07 | -1.1349e-09 | -1 | 0
2072 | 34.5333 | 5 | 12 | 5 | 12 | 70 | 40 | 1.6654e-07 | 3.5478 | 1.5612e-09 | 2.3168e-06 | 4.8 | 0 | 4.8 |  | 15.2 | 4 | 15.2 | 70 | 35 | 15 | 35 | -3.2327e-06 | -0.00051727 | 1.6654e-07 | -9.7575e-10 | -1 | 0
[25 empty] | 13.1105 |  |  | 24
0.10411
[24 empty] | First Quartile | 2.6302e-06
[24 empty] | Second Quartile | 7.5426e-05
[24 empty] | Third Quartile | 0.0021499
[24 empty] | MaxTrail | 1.6654e-07
CONTROL LEVEL SIMULATION
CONTROLLER
PROCESS
∑24_(𝑖=0)^𝑡▒(𝐸_𝑖 )
𝐸_𝑖
𝐸_𝑖−𝐸_(𝑖−1)
Fin, mc/h
Fout, mc/h
CYLINDRICAL TANK